## Dashboard
MONITORING AVAILABILITY IMPROVEMENT & VISIT SITE SPS
NOP Palangkaraya (PLK) · R08 Kalimantan ¦ Kurva S Target (Plan) vs Actual ¦ Satu file monitoring bersama
Tanggal update | 2026-10-11 |  | Minggu berjalan | W41 |  | Filter Site Class |  | (Semua) | Filter Main Power |  | (Semua) | Filter Action Plan |  | (Semua)
Sel kuning = dropdown filter. Tanggal update otomatis (=TODAY()); ganti dengan tanggal tetap bila ingin snapshot.
A. AVAILABILITY IMPROVEMENT & REPETITIVE (Tracker Improvement)
TOTAL SITE |  | DONE |  | ON GOING |  | OPEN |  | % DONE |  | PLAN s.d. MINGGU INI |  | ACTUAL s.d. MINGGU INI |  | ACHIEVEMENT
223 |  | 49 |  | 0 |  | 174 |  | 21.97% |  | 70 |  | 45 |  | 64.29%
sesuai filter |  | status final |  | sedang dikerjakan |  | belum selesai |  | Done / Total site |  | kumulatif s.d. W41 |  | kumulatif s.d. W41 |  | Actual / Plan (target ≥100%)
Progres per Action Category (10 terbesar)
[10 empty] | Action Category |  | Total | Done | Open* | % Done
[10 empty] | Rectifier & Battery System |  | 114 | 6 | 108 | 5.263%
[10 empty] | Need Visit On site |  | 27 | 7 | 20 | 25.93%
[10 empty] | Impact Hub |  | 15 | 7 | 8 | 46.67%
[10 empty] | Need Upgrade SPS |  | 15 | 7 | 8 | 46.67%
[10 empty] | Need Upgrade SPS & Perbaikan Genset |  | 8 | 4 | 4 | 50%
[10 empty] | Genset Rectification |  | 7 | 4 | 3 | 57.14%
[10 empty] | Eskalasi Listrik Corporate |  | 6 | 1 | 5 | 16.67%
[10 empty] | SPS TP Improvement |  | 5 | 0 | 5 | 0%
[10 empty] | SPS Tsel Recovery |  | 4 | 2 | 2 | 50%
[10 empty] | PSB PLN |  | 3 | 2 | 1 | 66.67%
[10 empty] | Lainnya |  | 19 | 9 | 10 | 47.37%
[10 empty] | TOTAL |  | 223 | 49 | 174 | 21.97%
*Open = Open + On Going
Progres per Site Class & Status Plan | [8 empty] | Cek Kualitas Data (otomatis)
Site Class | Total | Done | On Going | Open | Belum ada plan | Plan s.d. minggu ini | % Done |  | Duplikat SITEID di Tracker | [5 empty] | 0
DIAMOND | 3 | 1 | 0 | 2 | 0 | 3 | 33.33% |  | DONE tanpa Date Actual | [5 empty] | 1
PLATINUM | 38 | 7 | 0 | 31 | 20 | 15 | 18.42% |  | Ada Date Actual, status belum DONE | [5 empty] | 2
GOLD | 84 | 12 | 0 | 72 | 52 | 26 | 14.29% |  | Reschedule (Date Plan > Week Target) | [5 empty] | 12
SILVER | 33 | 10 | 0 | 23 | 21 | 9 | 30.3% |  | Site belum punya plan (TBD/kosong) | [5 empty] | 126
BRONZE | 65 | 19 | 0 | 46 | 37 | 17 | 29.23% |  | Visit SPS Overdue (lewat plan, belum visit) | [5 empty] | 7
TOTAL | 223 | 49 | 0 | 174 | 130 | 70 | 21.97% |  | Data di luar jangkauan formula (Tracker > baris 1004) | [5 empty] | 0
Detail per site lihat kolom "Flag Data" (AJ) di sheet Tracker Improvement.
B. VISIT SITE SPS — NOP PALANGKARAYA (Jadwal Visit SPS)
TOTAL SITE VISIT |  | SUDAH VISIT |  | PLANNED |  | OVERDUE |  | BELUM DIJADWALKAN |  | % VISIT DONE |  | PLAN s.d. HARI INI |  | ACHIEVEMENT VISIT
34 |  | 11 |  | 15 |  | 7 |  | 1 |  | 32.35% |  | 15 |  | 73.33%
site SPS NOP PLK |  | Actual Date terisi |  | jadwal ke depan |  | lewat plan, belum visit |  | perlu plan date |  | Visit / Total site |  | kumulatif |  | Visit / Plan s.d. hari ini
Status Visit per Action Plan
[10 empty] | Action Plan | Total | Done | Planned | Overdue | Belum jadwal
[10 empty] | Need SPS Recovery | 19 | 5 | 9 | 5 | 0
[10 empty] | Need Upgrade SPS | 15 | 6 | 6 | 2 | 1
[10 empty] | TOTAL | 34 | 11 | 15 | 7 | 1
Plan Visit per Minggu
[10 empty] | Minggu |  | Plan | Done | Sisa | % Done
[10 empty] | W36 (31/08–06/09) |  | 0 | 0 | 0 | 0%
[10 empty] | W37 (07/09–13/09) |  | 0 | 0 | 0 | 0%
[10 empty] | W38 (14/09–20/09) |  | 2 | 2 | 0 | 100%
[10 empty] | W39 (21/09–27/09) |  | 0 | 0 | 0 | 0%
[10 empty] | W40 (28/09–04/10) |  | 6 | 4 | 2 | 66.67%
[10 empty] | W41 (05/10–11/10) |  | 7 | 1 | 6 | 14.29%
[10 empty] | W42 (12/10–18/10) |  | 13 | 2 | 11 | 15.38%
[10 empty] | W43 (19/10–25/10) |  | 4 | 2 | 2 | 50%
[10 empty] | W44 (26/10–01/11) |  | 1 | 0 | 1 | 0%
Kurva S: garis putus-putus = Plan/Target kumulatif (baseline), garis tegas = Actual kumulatif. Baris kuning di tabel = minggu/hari berjalan.
Note on J4: Pilih dari dropdown. Memengaruhi KPI, Kurva S, dan tabel improvement.
Note on P4: Filter bagian B (Visit SPS): Need SPS Recovery / Need Upgrade SPS.

## Tracker Improvement
TRACKER AVAILABILITY IMPROVEMENT & REPETITIVE — NOP PALANGKARAYA
Sumber: All Tracking Availability Improvement Repetitive W38 (sheet Site List). Kolom putih = input; kolom biru muda (AE–AJ) = formula otomatis, jangan diketik.
No | SITEID | SITE NAME | DEPARTEMEN | SITE CLASS | Main Power | Backup | Repetitive 109 | DPG 429 | H2 Area 1133 + 332 | Red Site 1921 (254) | Irisan (jml program) | Denum | Range Denum | RC Category | RC Tier | RC Detail | Action Cat | Action Detail | Support Needed | Feedback NOP | Week Target | Effort Cat | Impact Cat | Action Status | Availability Status | Date Plan | Date Actual | Xcheck H2 SOW | Remark | Plan Week (baseline) | Actual Week | Status Final | Plan Visit SPS | Actual Visit SPS | Flag Data
1 | BNT005 | BNT005_KALANISDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  | Yes | 2 | 1468783 | 1-2 Mio | Power | Baterai | APR ZTE hitam faulty 2pcs, waiting repair from TI_Lacking module APR ZTE/waiting process repair by TI | Rectifier & Battery System |  | Tshooting Power | Lacking module APR ZTE/waiting process repair by TI |  | High Effort | [5 empty] | Refinement FO Corporate |  |  |  | OPEN |  |  | Belum ada plan;
2 | BNT020 | BNT020_ADAROKLANIS | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  |  | Yes | 1 | 2591970 | 2-3 Mio | Transmisi | FO Telkom Putus | Aktivitas Pihak ke-3 | FO Cut Escalation |  | Escalate to corporate | done replace cable optik by corporate |  | High Effort |  | OPEN |  |  |  | FO_Corporate |  |  |  | OPEN |  |  | Belum ada plan;
3 | BNT025 | BNT025_RANGGAILUNGPTI | NOP PALANGKARAYA | BRONZE | PLN | PLN 12H + BATTERY | Yes |  |  |  | 1 | 1900778 | 1-2 Mio | Power | PLN Off | PLN 12 Jam, Existing 3P Lithium. | Rectifier & Battery System | Already PSB PLN 12 jam + new recty 3M3P | Add Battery 9p + Slave | PLN 12 Jam, propose Genset or add battery 9 pack (lesson learned TML032) | TBD | High Effort | Low Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
4 | BNT160 | N_BNT160_PASARPATASDMT | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  |  |  | Yes | 1 | 1641581 | 1-2 Mio | Power | PLN Off | Under investigate | Rectifier & Battery System |  | Swap System + Add Battery | PLN off lebih dari 3 jam, Battery 2P not back up and Rectifier problem | TBD | High Effort | Medium Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
5 | BNT195 | BNT195_BANGKUANG2DMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1727980 | 1-2 Mio | Power | Baterai | Pemadaman PLN > 3Jam, Battery 1p faulty, BBT stil 4 jam_Swap battery 1p, claim battery 1p | Rectifier & Battery System |  | Add Battery 1p | Swap battery 1p, claim battery 1p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
6 | COH670 | C_COH670_MIDESATUMBANGRANDANGTSEL | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  |  | Yes | 1 | 691192 | < 1 Mio | PLN | PLN Off | Under investigate | Rectifier & Battery System |  | Add Battery 2p | Need add battery 2p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
7 | COH902 | C_COH902_PTHPUBDASCO | NOP PALANGKARAYA | PLATINUM | CORPORATE | BATTERY |  |  | Yes |  | 1 | 1641581 | 1-2 Mio | Power | Rectifier | swap battery 3P MTW037 | Rectifier & Battery System |  | Impact Hub | Swap battery 3P di MTW037 |  | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
8 | COH955 | C_COH955_PTTAMTAMAPERKASATSEL | NOP PALANGKARAYA | BRONZE | PLN | BATTERY |  |  | Yes |  | 1 | 777591 | < 1 Mio | Power | Rectifier | Upgrade battery with rack slave / add new system | Rectifier & Battery System |  | Add Battery 2p | Need add battery 2p | TBD | High Effort | Low Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
9 | COH956 | C_COH956_PTAGU MILLBUTONGTSEL | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  |  | Yes |  | 1 | 777591 | < 1 Mio | Power | Rectifier | Escalation to TIF | Rectifier & Battery System |  | Add Battery 2p | Need add battery 2p | TBD | High Effort | Medium Impact | OPEN |  |  |  | Refinement FO Telkom |  |  |  | OPEN |  |  | Belum ada plan;
10 | KKN004 | KKN004_TUMBANGTALAKEN | NOP PALANGKARAYA | PLATINUM | PLN | GENSET |  | Yes | Yes |  | 2 | 2419172 | 2-3 Mio | Power | Genset | genset manual problem module genset faulty_Perbaikan ats modul via sva (waiting approval nos) | Genset Rectification |  | Rektifikasi Genset | Perbaikan ats modul via sva (waiting approval nos) |  | Low Effort |  | DONE |  | 2026-09-20 | 2026-09-20 | Rektifikasi Genset | Done rewairing genset dan replace module | 38 | 38 | DONE
11 | KKN005 | KKN005_TUMBANGMIRI | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 2591970 | 2-3 Mio | Power | PLN Off | •Arester ACPDB NOK •Arester rectifire 1 NOK, Bar grond indoor NOK •Bar grond tower NOK •Downconductor NOK •Neon Shelter NOK •Exhausfan NOK_Helathy check battery, enva simulation | Impact Hub |  | Impact Hub | Helathy check battery, enva simulation OK, impact fo cut KKN054_KKN081 |  | Medium Effort |  | OPEN |  | 2026-10-05 |  |  |  | 41 |  | OPEN
12 | KKN011 | KKN011_KAMPURI | NOP PALANGKARAYA | GOLD | PLN | GENSET |  | Yes |  |  | 1 | 2591970 | 2-3 Mio | Power | Baterai | 6P Lithium ZTE (3 NOK), Simualsi backup NOK (Batrei BTS tidak mampu hanya 1 bank). Genset Altenator NOK, Genset masih menggunakan tangki harian kapasitas 62 liter, Genset aresrer NOK_Rektifikasi Genset | Rectifier & Battery System | Penambahan tangki drum (waiting approval nos), Change wiring (waiting RAB), Display RH (Waiting RAB), module controler smartgen via SVA , rewiring, COS OK, no key genset, revisit by support darli | Genset Rectification | ATS genset problem have issue pcb, Need Display RH | W41 | High Effort | [7 empty] | 41 |  | OPEN
13 | KKN012 | KKN012_TMBGMIWANTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 2073576 | 2-3 Mio | Power | Baterai | SC200 faulty_Rektifikasi Rectifier | Rectifier & Battery System |  | Replace SC | Modul SC Faulty, propose replace | W40 | High Effort | [7 empty] | 40 |  | OPEN
14 | KKN013 | KKN013_TANJUNGKARITAKTBG | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes |  |  | 1 | 2073576 | 2-3 Mio | Power | Baterai | Battrey 2p fautly_Rebalancing load ,ambil data log, claim battery 2p | Rectifier & Battery System |  | Add Battery 2p | Rebalancing load ,ambil data log, claim battery 2p | W40 | High Effort | High Impact | OPEN | [5 empty] | 40 |  | OPEN
15 | KKN019 | KKN019_SEPANGPTI | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes |  |  | 1 | 2937566 | 2-3 Mio | Power | Baterai | Battrey 8p faulty_swab 2p battery, claim battery 8p | Rectifier & Battery System |  | Warranty Battery claim | swab 2p battery, claim battery 8p | TBD | High Effort | High Impact | [8 empty] | OPEN |  |  | Belum ada plan;
16 | KKN020 | N_KKN020_TANGKAHENDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 2073576 | 2-3 Mio | Power | Baterai | 2p nok dari 4p_claim batt 2p | Rectifier & Battery System |  | Add Battery 2p | claim batt 2p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
17 | KKN021 | KKN021_RABAMBANGDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1641581 | 1-2 Mio | Power | Baterai | Battery 4p faulty_swap battery 4p | Rectifier & Battery System |  | Add Battery 2p | swap battery 4p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
18 | KKN027 | KKN027_JALANPOROSFAJARHARAPANPTI | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes | Yes |  | 2 | 1727980 | 1-2 Mio | Power | Baterai | Upgrade Module ZTE3000 & Battery by TI | Rectifier & Battery System |  | Add Battery 1p | Replace modul apr, swab battery 1p from PPS101, claim battery | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
19 | KKN029 | KKN029_TUMBANGEMPAS2PTI | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes |  |  | 1 | 2073576 | 2-3 Mio | Power | Baterai | Enva NOK_replace SC, waiting part delivery to cluster plan 17-sep-26 | Rectifier & Battery System |  | Tshooting Power | replace SC, waiting part delivery to cluster plan 17-sep-26 | W40 | High Effort | [7 empty] | 40 |  | OPEN
20 | KKN033 | KKN033_TARINGENTBG | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes |  |  | 1 | 1987177 | 1-2 Mio | Power | Baterai | BBT 3 jam, Add new system by CR_Add new system | Rectifier & Battery System |  | Add New System | Add new system | TBD | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
21 | KKN034 | KKN034_MANUHINGTBG | NOP PALANGKARAYA | GOLD | IN BUILDING | BATTERY |  |  |  | Yes | 1 | 1987177 | 1-2 Mio | Transmisi | Impact Simpul | impact simpul KKN033 pemadaman PLN | Impact Hub |  | Add Battery 2p | swap batt 2P claim battrey | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
22 | KKN049 | KKN049_HURUNGBUNUTTBG | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  |  | Yes |  | 1 | 1900778 | 1-2 Mio | Power | Rectifier | Swap Battery 3p | Rectifier & Battery System |  | Swap battrey 3P | propose add battery 3p | TBD | High Effort | [5 empty] | Swap System |  |  |  | OPEN |  |  | Belum ada plan;
23 | KKN055 | KKN055_SIMPANGMIWAN | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes |  |  | 1 | 2937566 | 2-3 Mio | Power | Baterai | Battrey 4p faulty_Rebalancing load ,ambil data log, claim battery 4p | Rectifier & Battery System |  | Add Battery 4p | Rebalancing load ,ambil data log, claim battery 4p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
24 | KKN064 | KKN064_ANTANGTEWAHSTP | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 2159975 | 2-3 Mio | Power | Baterai | Battery 2p faulty_swap battery 2p. Work around Rebalancing Battery | Rectifier & Battery System | Rebalancing Battery | Add Battery 2p | Swap battery 2p | W39 | High Effort | High Impact | OPEN |  | 2026-10-01 | 2026-10-01 |  | Replace 2p Baterai | 39 | 40 | DONE |  |  | Ada Date Actual, status belum DONE; Reschedule (Date Plan > Week Target);
25 | KKN071 | KKN071_BELAWANMULYADMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 2591970 | 2-3 Mio | Power | Baterai | PLN OFF > 3 jam, BBT 1 Jam | Rectifier & Battery System |  | Add Battery 3p | Claim battery 3p, Replace Sc200 | W40 | High Effort | High Impact | OPEN | [5 empty] | 40 |  | OPEN
26 | KKN074 | KKN074_DSTUMBANGDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 2073576 | 2-3 Mio | Power | Baterai | batt tidak ada_add battrey 2p | Rectifier & Battery System |  | Add Battery 2p | add battrey 2p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
27 | KKN075 | KKN075_KENDETDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  | Yes | 2 | 1814379 | 1-2 Mio | Power | Baterai | 2p battrey nok | Rectifier & Battery System |  | Add Battery 2p | claim batt 2p | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
28 | KKN222 | KKN222_FLORANUSAPERDANAPST | NOP PALANGKARAYA | GOLD | CORPORATE | BATTERY |  | Yes | Yes | Yes | 3 | 1641581 | 1-2 Mio | Power | Corporate | Power Corporate Off | Rectifier & Battery System | Claim battery, Upgrade battery 3p (CLOSED) | Add Battery 2p | Swap batt 2P, claim battery 2p | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery | Add 2p Baterai |  |  | DONE
29 | KKN223 | KKN223_ARCHIPELAGOSTP | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  |  | Yes |  | 1 | 2505571 | 2-3 Mio | Power | Baterai | Escalation to TIF | Rectifier & Battery System |  | Warranty Battery claim | Rebalancing load ,ambil data log, claim battery | W40 | High Effort | High Impact |  |  |  |  | Refinement FO Telkom |  | 40 |  | OPEN
30 | KKN230 | KKN230_MULIASAWITAGROLESTARITBG | NOP PALANGKARAYA | GOLD | IN BUILDING | BATTERY |  | Yes |  |  | 1 | 2332773 | 2-3 Mio | Power | Corporate | Power Corporate Off | Rectifier & Battery System | Upgrade Battery 0M2P | Add Battery 2p | claim batt 2p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
31 | KKN231 | KKN231_AGROLESTARISENTOSATBG | NOP PALANGKARAYA | PLATINUM | CORPORATE | BATTERY |  |  |  | Yes | 1 | 2073576 | 2-3 Mio | Power | Corporate | Power CORPORATE OFF | Rectifier & Battery System |  | Add Battery 3p | Rebalancing load ,ambil data log, claim battery 1p, add battery 3p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
32 | KKP013 | KKP013_BATUNINDAN | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1900778 | 1-2 Mio | Power | PLN Off | PLN Off > 3Jam BBT 1jam | Rectifier & Battery System |  | Add Battery 2p | Upgrade battery 2P | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
33 | KKP018 | KKP018_PENDAMUNTEITBG | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes | Yes |  | 2 | 1814379 | 1-2 Mio | Power | Baterai | CSU faulty, Kabel battery stolen, PLN low voltage_Replace csu & install kabel power battery (install AVR) | Rectifier & Battery System |  | Tshooting Power | Replace csu & install kabel power battery (install AVR) |  | High Effort | [5 empty] | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
34 | KKP026 | KKP026_LAMUNTI | NOP PALANGKARAYA | SILVER | PLN | GENSET |  |  | Yes |  | 1 | 1641581 | 1-2 Mio | Power | Rectifier | Swap battery 4P | Rectifier & Battery System |  | Add Battery 4p | PLN off lebih dari 3 jam, Battery not back up | TBD | High Effort | Medium Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
35 | KKP027 | KKP027_PUJONTBG | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes | Yes |  | 2 | 2332773 | 2-3 Mio | Power | Baterai | Kabel power battery stolen, PLN low voltage, upgrade battery 1P | Rectifier & Battery System |  | Add Battery 2p | Install kabel power battery & upgrade 2P battery from ex sps hybrid | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Swap Battery |  |  |  | OPEN |  |  | Belum ada plan;
36 | KKP031 | KKP031_GADABUNGTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 1814379 | 1-2 Mio | Transmisi | Impact Simpul | Impact PPS031 Battery not back up vrla floating_Swap battery at hub pps031, impact hub | Impact Hub |  | Impact Hub | Swap battery at hub pps031, impact hub |  | Medium Effort | [6 empty] | Need Battery |  |  | OPEN |  |  | Belum ada plan;
37 | KKP034 | KKP034_TBKATUNJUNGTBG | NOP PALANGKARAYA | BRONZE | GENSET | SPS |  |  | Yes | Yes | 2 | 1036788 | 1-2 Mio | Power | Genset | Pengecekan Genset dan Relok battery | BBM Management |  | BBM Readyness | Genset no issue, need monitoring BBM Readyness |  | Low Effort |  | DONE |  | 2026-10-07 | 2026-10-08 |  | Done add tanki 200L | 41 | 41 | DONE
38 | KKP035 | KKP035_SAKATAMIANGTBG | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  | Yes |  |  | 1 | 1814379 | 1-2 Mio | Power | Baterai | Battery VRLA drop_Swap battery 2p | Rectifier & Battery System |  | Add Battery 2p | Swap battery 2p | TBD | High Effort | Medium Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
39 | KKP039 | KKP039_SUKAMAJUTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1641581 | 1-2 Mio | Power | Baterai | Pemadaman PLN > 3Jam, battery 2p faulty_swap 2p battery, claim battery 2p | Rectifier & Battery System |  | Add Battery 2p | swap 2p battery, claim battery 2p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
40 | KKP044 | KKP044_KAYUBULANPTI | NOP PALANGKARAYA | PLATINUM | PLN | GENSET |  | Yes | Yes |  | 2 | 3283162 | > 3 Mio | Power | Baterai | Battery 2p faulty for bts, genset aki drop, timer, relay problem_Swap battery transmisi 2P, autonisasi genset | Rectifier & Battery System |  | Add Battery 2p | Swap battery transmisi 2P, autonisasi genset |  | High Effort | High Impact | DONE |  | 2026-10-07 | 2026-10-10 | Swap Rectifier & Upgrade Battery | Genset done auto ,problem digenset diakuator sudah dibawa ke palangkaraya untuk diservice | 41 | 41 | DONE
41 | KKP045 | KKP045_TRANTANGPTI | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 1814379 | 1-2 Mio | Power | Baterai | Pemadaman PLN > 3Jam, battery 2p faulty_Swap battery 2p, Claim Battery | Rectifier & Battery System |  | Add Battery 2p | Swap battery 2p, Claim Battery |  | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
42 | KKP046 | KKP046_MARAPITPTI | NOP PALANGKARAYA | PLATINUM | PLN | GENSET |  | Yes |  |  | 1 | 2246374 | 2-3 Mio | Power | Baterai | Battery 1p faulty, 5p Battery OK, genset sering masuk angin_Swap system (recty) and perbaikan genset, claim battery 1p | Rectifier & Battery System |  | Tshooting Genset | Swap system (recty) and perbaikan genset, claim battery 1p |  | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
43 | KKP050 | KKP050_BUMIRAHAYUTBG | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  | Yes | Yes |  | 2 | 1555182 | 1-2 Mio | Transmisi | Impact Simpul | Transmisi, impact KKP025_Done replace MCB battery di KKP025 | Impact Hub |  | Impact Hub | Done replace MCB battery di KKP025 |  | Medium Effort |  | DONE |  | 2026-08-05 | 2026-08-05 | Upgrade Module & Battery |  | 32 | 32 | DONE
44 | KKP052 | KKP052_IAAS_KRSSITEKSRTBG | NOP PALANGKARAYA | GOLD | CORPORATE | BATTERY |  | Yes | Yes |  | 2 | 1209586 | 1-2 Mio | Power | Baterai | Battery 2p OK_Add battery 2p | Rectifier & Battery System |  | Add Battery 2p | Add battery 2p |  | High Effort | High Impact | OPEN |  |  |  | Refinement FO Telkom |  |  |  | OPEN |  |  | Belum ada plan;
45 | KKP055 | C_KKP055_MVPASARTIMPAHPTI | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 950389 | < 1 Mio | Power | Baterai | Pemadaman PLN >3 jam, No Battery_Add battery 2p | Rectifier & Battery System |  | Add Battery 2p | Add battery 2p |  | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
46 | KKP065 | KKP065_LUNGKOHLAYANGTBG | NOP PALANGKARAYA | DIAMOND | PLN | BATTERY |  | Yes |  |  | 1 | 3542359 | > 3 Mio | Power | Genset | PLN Off > 3 Jam impact Karhutla, kondisi PLN sering drop voltage_New Genset | Genset Rectification |  | Troubleshoot Rectifier & Upgrade daya | Site Diamond single recty hariff, propose perbaikan backplane recti faulty ZTE & Propose upgrade daya 23000 kva |  | Low Effort |  | DONE |  | 2026-10-10 | 2026-10-10 | Upgrade Module & Battery | Perlu add battery,dan penambahan module 3 | 41 | 41 | DONE
47 | KKP066 | KKP066_PETAKPTIDMT | NOP PALANGKARAYA | SILVER | SPS TP | BATTERY |  |  | Yes |  | 1 | 1468783 | 1-2 Mio | Power | Solar Cell | SPS TP | SPS TP Improvement |  | Add Genset | SPS TP DMT, propose genset backup power |  | Medium Effort | [6 empty] | Under TP |  |  | OPEN |  |  | Belum ada plan;
48 | KKP067 | KKP067_BKITBATUDMT | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes |  |  | 1 | 2851167 | 2-3 Mio | Power | Baterai | Pemadaman PLN > 3jam battery backup 3 jam | Rectifier & Battery System |  | Add Battery 2p | Upgrade 2P battery for TRM and propose install genset due hub site telkom dwdm , moving load equipment dwdm to TRM recti |  | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
49 | KKP068 | KKP068_DANAURAWAHDMT | NOP PALANGKARAYA | GOLD | SPS TP | BATTERY | Yes |  | Yes |  | 2 | 1641581 | 1-2 Mio | Power | Solar Cell | SPS TP DMT MCB Issue | SPS TP Improvement |  | Add Genset | SPS TP DMT, propose genset backup power |  | Medium Effort | [6 empty] | Under TP |  |  | OPEN |  |  | Belum ada plan;
50 | KKP069 | KKP069_TUMBANGTUKUNTBG | NOP PALANGKARAYA | BRONZE | SPS TP | BATTERY | Yes |  | Yes |  | 2 | 1814379 | 1-2 Mio | Power | Solar Cell | CDC TI Issue. BBM Issue SPS TP TBG : sudah di CO, tapi UPS Rusak | Convert to SPS TP |  | Add Genset | SPS TP TBG, propose genset backup power |  | High Effort | Medium Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
51 | KKP070 | N_KKP070_IMACRO_B2BTIMURSATRIAPERKASASCO | NOP PALANGKARAYA | SILVER | CORPORATE | BATTERY |  |  | Yes |  | 1 | 691192 | < 1 Mio | Power | Corporate | Power Corporate Off | Rectifier & Battery System | Upgrade Module & Battery 2M2P | Add Battery 2p | Power corporate, site langsung down, Propose add battery 2p and modul APR |  | High Effort | Medium Impact | OPEN |  |  |  | Refinement FO Telkom |  |  |  | OPEN |  |  | Belum ada plan;
52 | KKP072 | KKP072_BAJUHDMT | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes | Yes |  | 2 | 2246374 | 2-3 Mio | Power | Baterai | CSU faulty, 3P battery faulty (PLN low voltage) | Rectifier & Battery System | Done replace CSU | Replace CSU | Done replace CSU, need swap battery faulty 3P |  | High Effort |  | DONE |  | 2026-09-10 | 2026-09-10 | Upgrade Module & Battery | done tshoot dan add batterai | 37 | 37 | DONE
53 | KKP078 | C_KKP078_GRAHAINTIDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1987177 | 1-2 Mio | Power | Baterai | Power corporate need to check battery condition_Swap battery 2p | Rectifier & Battery System |  | New System | Propose new system & battery 2p |  | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
54 | KKP080 | KKP080_KAYUBULANTBG | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes |  |  | 1 | 1987177 | 1-2 Mio | Power | PLN Off | PLN off > 3 jam, BBT 3-4 jam, Site flicker due to pln drop voltage_escalation to PLN additional trafo done | PLN Escalation |  | Escalate PLN | escalation to PLN additional trafo done |  | Low Effort |  |  |  | 2026-10-11 |  |  |  | 41 |  | OPEN
55 | KKP082 | KKP082_HURUNGPUKUNGTBG | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes | Yes |  | 2 | 1727980 | 1-2 Mio | Power | Baterai | PLN drop low voltage, Battery only 2p_Add battrey 2p | Rectifier & Battery System |  | Add Battery 2p | Add battrey 2p |  | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
56 | KKP087 | KKP087_DESAKALADAN | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 1641581 | 1-2 Mio | Transmisi | Impact Simpul | Impact KKP045 (fo cut), battery only 1p OK, 2p faulty disite KKP045_impact Hub KKP045 | Impact Hub |  | Impact Hub | impact Hub KKP045 |  | Medium Effort |  |  |  | 2026-10-07 |  |  |  | 41 |  | OPEN
57 | KKP088 | C_KKP088_IAASASMISECTOR4SCO | NOP PALANGKARAYA | BRONZE | CORPORATE | BATTERY | Yes |  | Yes |  | 2 | 1295985 | 1-2 Mio | Power | Corporate | Power Corporate Off | Eskalasi Listrik Corporate | Corporate escalation | Add Battery 2p | Power corporate Tower Corporate, Batrei 2 bank backup, ok Enva valid |  | High Effort | Low Impact | OPEN |  |  |  | Vandalisme |  |  |  | OPEN |  |  | Belum ada plan;
58 | KKP090 | KKP090_IMACRO_ASMINBARABARONANGPTI | NOP PALANGKARAYA | DIAMOND | CORPORATE | BATTERY |  |  | Yes |  | 1 | 4233551 | > 3 Mio | Transmisi | Impact Simpul | Impact Simpul KKP065 down. PLN Undervoltage, propose genset | Impact Hub | Impact Simpul KKP065 down. PLN Undervoltage, propose genset | New Genset | Impact KKP065 diamond hubsite, propose Genset |  | Medium Effort |  | OPEN |  | 2026-10-08 |  |  |  | 41 |  | OPEN
59 | KKP092 | KKP092_IAAS_WANACATURJAYAUTAMATBG | NOP PALANGKARAYA | GOLD | CORPORATE | BATTERY |  | Yes | Yes |  | 2 | 1295985 | 1-2 Mio | Transmisi | Impact Simpul | Impact KKP072. PLN Undervoltage. Plan AVR | Impact Hub | Impact KKP072. PLN Undervoltage. Plan AVR | Impact Hub | done rebalancing recty transmisi di KKP072 |  | Medium Effort |  | DONE |  | 2026-09-10 | 2026-09-10 |  |  | 37 | 37 | DONE
60 | KKP094 | KKP094_MANDOMAI | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  |  | Yes | 1 | 1814379 | 1-2 Mio | Power | PLN Off | Pemadaman PLN > 3jam battery backup 1 jam | Rectifier & Battery System |  | Add Battery 2p | Swap battery |  | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
61 | KKP095 | KKP095_MANTANGAI | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 1987177 | 1-2 Mio | Power | Baterai | Pemadaman PLN >3jam, BBT 2jam, battry 4P, 2P faulty_Swap 2P battery faulty (claim warranty) | Rectifier & Battery System |  | Warranty Battery claim | Swap 2P battery faulty (claim warranty) | TBD | High Effort | High Impact |  |  |  |  | Refinement FO Telkom |  |  |  | OPEN |  |  | Belum ada plan;
62 | KKP098 | C_KKP098_COMBATPAMACPP | NOP PALANGKARAYA | BRONZE | CORPORATE | BATTERY |  |  | Yes |  | 1 | 518394 | < 1 Mio | Transmisi | Impact Simpul | Impact Simpul KKP065 down. PLN Undervoltage, propose genset | Impact Hub | Impact Simpul KKP065 down. PLN Undervoltage, propose genset | New Genset | Impact KKP065 diamond hubsite, propose Genset |  | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
63 | KKP101 | KKP101_BELANTISIAM | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  |  |  | Yes | 1 | 2073576 | 2-3 Mio | Power | PLN Off | PLN Off >3 Jam. BBT 2 jam | Rectifier & Battery System |  | New System | Impact KKP016 (BBT problem), Upgrade Battery, PLN sering mati, site susur sungai, upgrade new system, plan Apr 26 |  | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
64 | KKP102 | KKP102_BINJAYAPTI | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  | Yes | Yes |  | 2 | 2332773 | 2-3 Mio | Power | Baterai | 3P Battry Faulty_Swap battery 3P, Claim Battery 3p | Rectifier & Battery System |  | Add Battery 3p | Swap battery 3P, Claim Battery 3p |  | High Effort | Medium Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
65 | KKP119 | KKP119_IMACRO_DAMANGSIMAN | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes | Yes |  | 2 | 3715157 | > 3 Mio | Power | Baterai | PLN low votage , cabel power battery stolen, 4p still back up, Pln drop voltage_install kabel power battery & install AVR | Rectifier & Battery System |  | Tshooting Power | install kabel power battery & install AVR |  | High Effort | [5 empty] | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
66 | KKP212 | KKP212_B2BKAPUASMAJUJAYASCO | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  | Yes |  | 1 | 2332773 | 2-3 Mio | Transmisi | Impact Simpul | Impact KKP072. PLN Undervoltage. Plan AVR | Impact Hub | Impact KKP072. PLN Undervoltage. Plan AVR | Propose AVR |  |  | Medium Effort |  | DONE |  | 2026-09-10 | 2026-09-10 |  |  | 37 | 37 | DONE
67 | KKP217 | KKP217_N3TTABOREDMT | NOP PALANGKARAYA | BRONZE | SPS | GENSET | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Perlu pengadaan battery charger, agar aki tidak sering drop ¦ SVA Ready For FMS | Need Upgrade SPS & Perbaikan Genset | Perlu pengadaan battery charger, agar aki tidak sering drop ¦ SVA Ready For FMS | Genset Troubleshooting | Dinamo start Genset faulty (Done), Accu drop, Battery charger (SVA done), Need BBM Readyness | W39 | Medium Effort | Medium Impact | DONE |  | 2026-09-30 | 2026-10-08 |  | Done perbaikan RH dan auto serta penambahan pondasi dan Y selang tinggal ke pengisi BBM untuk menginfokan kapan diisi agar dapat melubangai tangki yang ada | 39 | 41 | DONE |  |  | Reschedule (Date Plan > Week Target);
68 | KKP218 | KKP218_N3TMASARANDMT | NOP PALANGKARAYA | PLATINUM | PLN | SPS |  | Yes |  |  | 1 | 1987177 | 1-2 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Tshooting Power | Battery 2p faulty claim warranty |  | Low Effort |  |  |  | 2026-10-11 |  |  |  | 41 |  | OPEN
69 | KKP220 | KKP220_N3TBATUSAMBUNGDMT | NOP PALANGKARAYA | SILVER | SPS | GENSET |  |  | Yes |  | 1 | 863990 | < 1 Mio | Power | Solar Cell | No Issue genset ¦ BBM Unmanaged | Need Upgrade SPS & Perbaikan Genset | No Issue genset ¦ BBM Unmanaged | BBM Readyness | Genset no issue |  | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
70 | KKP225 | KKP225_TAPENDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 2678369 | 2-3 Mio | Power | Baterai | PLN sering tidak stabil, 4P battery faulty, 3p new battery need healthy check_Swap battery 4P, claim Battery | Rectifier & Battery System | TroubleShoot Kabel Power Battery | Add Battery 4p | Swap battery 4P, claim Battery | W39 | High Effort | High Impact | DONE |  | 2026-10-01 | 2026-10-01 | Upgrade Module & Battery | done pemasangan kabel baterai | 39 | 40 | DONE |  |  | Reschedule (Date Plan > Week Target);
71 | KKP227 | KKP227_N3TLAWANGKAJANGDMT | NOP PALANGKARAYA | GOLD | PLN | SPS |  | Yes |  |  | 1 | 1468783 | 1-2 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Tshooting Power | Need allocation New system site PSB still using old recti |  | Low Effort |  | OPEN |  | 2026-10-12 |  |  |  | 42 |  | OPEN
72 | KKP293 | N_KKP293_N3TTUMBANGMUROIDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  | Troubleshoot SPS | Switch off L18, L21 (Lock SW Done) S2 |  | Medium Effort | Medium Impact | OPEN |  | 2026-10-09 |  |  |  | 41 |  | OPEN | 2026-10-10
73 | KKP304 | N_KKP304_N3TRAHUNGBUNGAIDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 691192 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | PSB PLN |  | PLNisasi | Jaringan PLN sudah tersedia, propose PLNisasi |  | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
74 | KKP305 | KKP305_N3TSEIAHASDMT | NOP PALANGKARAYA | SILVER | SPS | GENSET | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Aki genset drop ¦ SVA Ready For FMS | Need Upgrade SPS & Perbaikan Genset | Aki genset drop ¦ SVA Ready For FMS |  |  |  | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
75 | KKP306 | KKP306_N3TTUMBANGMANGKUTUPDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 518394 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | High Effort | Medium Impact | OPEN | [7 empty] | OPEN | 2026-10-10 |  | Belum ada plan;
76 | KKP310 | KKP310_N3TBALAIBANJANGDMT | NOP PALANGKARAYA | SILVER | PLN | SPS |  |  | Yes |  | 1 | 863990 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | Low Effort |  | DONE |  | 2026-10-05 | 2026-10-10 |  | Baterai aman backup aman | 41 | 41 | DONE
77 | KKP311 | KKP311_N3THURUNGKAMPINDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  |  |  |  | High Effort | [9 empty] | OPEN | 2026-10-03 |  | Belum ada plan;
78 | KKP314 | KKP314_N3TSEIRINGINDMT | NOP PALANGKARAYA | SILVER | SPS | GENSET | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | SPS CSU Problem. Relay faulty,BBM Empty | Need Upgrade SPS & Perbaikan Genset | SPS CSU Problem. Relay faulty,BBM Empty |  |  |  | High Effort | [9 empty] | DONE
79 | KKP315 | KKP315_SEITERASTBG | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 1641581 | 1-2 Mio | Power | Baterai | Pemadaman PLN > 3jam, Battery 4P faulty_Swap battery 4p | Rectifier & Battery System |  | Add Battery 4p | Swap battery 4p |  | High Effort | Medium Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
80 | KKP323 | KKP323_B2BKMJMHESCO | NOP PALANGKARAYA | SILVER | CORPORATE | BATTERY |  |  | Yes |  | 1 | 1814379 | 1-2 Mio | Transmisi | Impact Simpul | Impact KKP072. PLN Undervoltage. Plan AVR | Impact Hub | Impact KKP072. PLN Undervoltage. Plan AVR |  |  |  | Medium Effort |  | DONE |  | 2026-09-10 | 2026-09-10 |  |  | 37 | 37 | DONE
81 | KKP325 | N_KKP325_N3TTANJUNGRENDANDMT | NOP PALANGKARAYA | SILVER | SPS | BATTERY |  |  | Yes |  | 1 | 691192 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  |  |  |  | High Effort | [9 empty] | OPEN | 2026-10-18 |  | Belum ada plan;
82 | KKP326 | KKP326_TIMPAHTBG | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 2851167 | 2-3 Mio | Power | Baterai | Battery 2P BBT 1,5 jam impact PLN Off >3jam_Upgrade battery 3P | Rectifier & Battery System |  | Add Battery 3p | Upgrade battery 3P |  | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
83 | KKP340 | N_KKP340_B2BGLOBALINDOAGUNGLESTARIESTATEPLASMASCO | NOP PALANGKARAYA | GOLD | CORPORATE | BATTERY |  | Yes |  |  | 1 | 1814379 | 1-2 Mio | Power | Corporate | Power Corporate Off | Rectifier & Battery System | Listrik Corporate Down > 3 JAM BBT 1 JAM Power corporate by PLN Current Battery 2P (1 Broken) | Add Battery 2p | Upgrade battery transmisi 2P di KKP093 |  | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
84 | KKP342 | N_KKP342_B2BKAPUASMAJUJAYASITEPKSSCO | NOP PALANGKARAYA | SILVER | CORPORATE | BATTERY |  | Yes | Yes |  | 2 | 1641581 | 1-2 Mio | Transmisi | Impact Simpul | Impact KKP220 (SPS ) Impact KKP072 (UG Module & Battery done), MCB sering Trip karena PLN Low Voltage | Impact Hub | Impact KKP220 (SPS ) Impact KKP072 (UG Module & Battery done), MCB sering Trip karena PLN Low Voltage | Impact Hub | Healthiness genset KKP220 |  | Medium Effort |  | DONE |  | 2026-09-07 | 2026-09-07 |  |  | 37 | 37 | DONE
85 | KSN001 | KSN001_TUMBANGSENAMAN | NOP PALANGKARAYA | PLATINUM | PLN | GENSET |  |  | Yes |  | 1 | 2505571 | 2-3 Mio | Power | Genset | SVA assigned accu dan solenoid replace | Rektifikasi Genset |  | Impact Hub | Perbaikan enva, healthy check battery, Maintain Hub KSN153 done new genset | TBD | Low Effort |  | OPEN |  | 2026-10-10 |  |  |  | 41 |  | OPEN
86 | KSN003 | KSN003_TUMBANGKAMAN | NOP PALANGKARAYA | PLATINUM | PLN | GENSET |  | Yes |  |  | 1 | 3196763 | > 3 Mio | Power | Baterai | Battrey 3p faulty, Genset still manual_Rebalancing load ,ambil data log, claim battery 3p | Rectifier & Battery System |  | Warranty Battery claim | Rebalancing load ,ambil data log, claim battery 3p | TBD | High Effort | High Impact | [8 empty] | OPEN |  |  | Belum ada plan;
87 | KSN008 | KSN008_PEGATAN | NOP PALANGKARAYA | GOLD | PLN | GENSET |  | Yes |  |  | 1 | 1987177 | 1-2 Mio | Radio | BTS | 14p battrey oke_Alarm Impact Service Clearing/ Celldown | Celldown |  | Add Battery 2p | Claim battery 2p | W40 | High Effort | High Impact | DONE |  | 2026-09-22 | 2026-09-22 |  | done visit dan bcp | 40 | 39 | DONE
88 | KSN024 | KSN024_RANTAUASEMTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  | Yes | Yes | 2 | 1814379 | 1-2 Mio | Power | Corporate | Power Corporate Off | Rectifier & Battery System | Upgrade Module & Battery 2M2P | Add Battery 2p | Swap batt 2P, claim battery 2p | TBD | High Effort | High Impact | OPEN |  |  |  | Refinement FO Telkom |  |  |  | OPEN |  |  | Belum ada plan;
89 | KSN028 | KSN028_DESATUMBANGKALEMEIDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 1641581 | 1-2 Mio | Power | PLN Off | Module SC200 Layar Blank (NOK) - Fotocell Tower dan Lampu Halaman (NOK) - Kawat berduri depan dan belakang lepas dari penyangga (NOK) - Box Panel KWH PLN Miring Kekanan (NOK) - Fan Rectifer (NOK) - Module Rectifier Apr48 (NOK) - Battery Maxlife Floating 1_replace Sc200 waiting part delivery to cluster plan 16-sep-26 | Troubleshoot Rectifier |  | Tshooting Power | replace Sc200 waiting part delivery to cluster plan 16-sep-26 | W39 | Low Effort |  | DONE |  | 2026-10-01 | 2026-10-01 | Refinement FO Telkom |  | 39 | 40 | DONE |  |  | Reschedule (Date Plan > Week Target);
90 | KSN032 | KSN032_RANTAUBANGKIANGTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  | Yes | 2 | 1814379 | 1-2 Mio | Power | PLN Off | •Power corporate •Enva N/A •Backup batrei OK •3 module ZTE OK •2 bank Lithium ZTE OK_Enva not valid need check on site plan 15-sep-26 | Eskalasi Listrik Corporate |  | Tshooting Power | Enva not valid need check on site plan 15-sep-26 | W39 | Medium Effort |  | DONE |  | 2026-10-03 | 2026-10-03 |  | Enva valid baterai good | 39 | 40 | DONE |  |  | Reschedule (Date Plan > Week Target);
91 | KSN036 | KSN036_MANGGODMT | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 3283162 | > 3 Mio | Power | Baterai | PLN drop low voltage_pelaporan pln done, Battery claim done | Rectifier & Battery System |  | Swap Battery | pelaporan pln done, Battery claim done | W39 | High Effort | [5 empty] | Swap Battery |  | 39 |  | OPEN
92 | KSN039 | KSN039_RGTANGKOTBG | NOP PALANGKARAYA | BRONZE | SPS TP | BATTERY | Yes |  | Yes |  | 2 | 950389 | < 1 Mio | Power | Solar Cell | SPS broken | SPS TP Improvement |  | Add Genset | SPS TP TBG, propose genset backup power | TBD | Medium Effort | [6 empty] | Under TP |  |  | OPEN |  |  | Belum ada plan;
93 | KSN042 | KSN042_TEWANGRANGKANGTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1814379 | 1-2 Mio | Power | PLN Off | 1p battrey tidak aktif, pln need upgrade daya PLN_propose upgrade daya untuk activation battery pln 6.6 kva 1 phase | Upgrade PLN |  | Tshooting power | propose upgrade daya untuk activation battery pln 6.6 kva 1 phase | W39 | Medium Effort |  |  |  | 2026-10-16 |  |  |  | 39 |  | OPEN |  |  | Reschedule (Date Plan > Week Target);
94 | KSN048 | KSN048_MANGGOSELATANPTI | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1814379 | 1-2 Mio | Power | Baterai | PLN off > 3jam, 11P battrey oke_Healthy check rectifier | Rectifier & Battery System |  | Tshooting Power | Healthy check rectifier | W39 | High Effort | [7 empty] | 39 |  | OPEN
95 | KSN055 | N_KSN055_HANTATIRINGESTATEPTI | NOP PALANGKARAYA | GOLD | GENSET | BATTERY |  |  | Yes |  | 1 | 2419172 | 2-3 Mio | Power | Genset | Genset Broken | Genset Rectification |  | Tshooting Genset | problem genset di coinplug body genset, tim Bsok on site untuk PMG ke 2 sekalian untuk pengecekan dan perbaikan gensetnya | W39 | Low Effort |  | DONE |  | 2026-10-01 | 2026-10-01 |  | Indikasi bocor komprses sudah di lakukan perbaikan sementara agar kebocoran tidak merembes | 39 | 40 | DONE |  |  | Reschedule (Date Plan > Week Target);
96 | KSN110 | KSN110_DESAASEMKUMBANGDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 2246374 | 2-3 Mio | Power | Baterai | Tegangan pln phase S hilang - sc200 faulty - nok, Impact KSN036, Battery 2p faulty | Rectifier & Battery System |  | Tshooting Power | replace SC200, waiting part delivery to cluster plan 17-sep-26, lapor pln mobile done | W39 | High Effort | [7 empty] | 39 |  | OPEN
97 | KSN126 | KSN126_DESAJAYAMAKMUR | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 1641581 | 1-2 Mio | Power | PLN Off | 2025_KSN126_NOP PALANGKARAYA_Upgrade Battery_0M2P_Closed_W28; 2026_KSN126_NOP PALANGKARAYA_Upgrade Battery_0M2P_Closed_W19, Upgrade PLN | Rectifier & Battery System |  | Tshooting Power | replace SC200, stock available sc300, waiting part delivery to cluster, Akses to site sulit sungai surut | W40 | High Effort |  | DONE |  | 2026-09-22 | 2026-09-22 | Upgrade Module & Battery | done visit dan bcp | 40 | 39 | DONE
98 | KSN135 | KSN135_DESASAMBAKATUNGTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1814379 | 1-2 Mio | Power | Baterai | Pemadaman PLN bbt 0 jam | Rectifier & Battery System |  | Add Battery 2p | Claim battrey 2p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
99 | KSN150 | KSN150_N3TPENDATANGGARINGBARUDMT | NOP PALANGKARAYA | SILVER | SPS | GENSET | Yes |  | Yes | Yes | 3 | 777591 | < 1 Mio | Power | Solar Cell | Genset problem, proses perbaikan genset ex KSN153 | Need Upgrade SPS & Perbaikan Genset | 1 Oct 2026 : Swap Rectifier Genset problem, proses perbaikan genset ex KSN153 | Rectifier Modernization | Rectifier LVD faulty, Already upgrade SPS, under monitor, bad avail due to impact Karhutla | TBD | High Effort |  | DONE |  | 2026-10-02 | 2026-10-11 |  | Done genset system lowbat,enva valid | 40 | 41 | DONE
100 | KSN153 | N_KSN153_N3TTUMBANGBEMBANDMT | NOP PALANGKARAYA | BRONZE | SPS | GENSET | Yes |  | Yes |  | 2 | 863990 | < 1 Mio | Power | Solar Cell | No Issue genset ¦ Battery BTS Drop. BBM Unmanaged | Troubleshoot Rectifier | No Issue genset ¦ Battery BTS Drop. BBM Unmanaged. New system (PO TI), ganti kabel JTR yg hybrid SPS ke Tembaga, cleaning PV | Swap Rectifier | New Genset CR from TML032, need monitor BBM readyness | TBD | High Effort |  | DONE |  | 2026-10-02 | 2026-10-02 | Rektifikasi Genset | Genset system timer 4 on 2 off | 40 | 40 | DONE
101 | KSN164 | KSN164_N3TBATUBANGODMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | SCC faulty 1 Unit, Total Baterai 11p (8 faulty 3 Good) 8p sudah di lepas | Need Upgrade SPS | SCC faulty 1 Unit, Total Baterai 11p (8 faulty 3 Good) 8p sudah di lepas | Add Battery 8p, Pengantian SCC faulty 1 Unit | Visit Done 16 Sept 2026. Total Baterai 11p (8 faulty 3 Good) 8p. Claim battery di daisy | TBD | High Effort | Low Impact | DONE |  | 2026-09-14 | 2026-09-14 |  | done permbersihan panel | 38 | 38 | DONE | 2026-09-16 | 2026-09-16
102 | KSN165 | KSN165_N3TKARUINGDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  | Need Visit On site TS SPS |  | W42 | High Effort |  | DONE |  | 2026-10-04 | 2026-10-04 |  | done permbersihan panel | 42 | 40 | DONE | 2026-10-04 | 2026-10-04
103 | KSN188 | KSN188_N3TTUMBANGLAMBI | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes |  | 2 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) | W42 | High Effort | Medium Impact | OPEN | [5 empty] | 42 |  | OPEN | 2026-10-03
104 | KSN193 | KSN193_N3TRANGANBAHEKANGDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) | W42 | High Effort | Medium Impact | OPEN | [5 empty] | 42 |  | OPEN | 2026-10-14
105 | KSN709 | KSN709_KM55PALANGKARAYA | NOP PALANGKARAYA | BRONZE | PLN | BATTERY |  |  | Yes |  | 1 | 777591 | < 1 Mio | Power | Rectifier | Swap 3p battery with litium | Rectifier & Battery System |  | Swap battreyy 4p |  | TBD | High Effort | [5 empty] | Swap System |  |  |  | OPEN |  |  | Belum ada plan;
106 | KSN711 | KSN711_BATUBADINDINGDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1641581 | 1-2 Mio | Power | Baterai | battrey 2p alarm 2p ok_Claim Battery 2p | Rectifier & Battery System |  | Add Battery 2p | Claim Battery 2p | W40 | High Effort | High Impact | OPEN | [5 empty] | 40 |  | OPEN
107 | KSN713 | KSN713_RANTAUASEMDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1641581 | 1-2 Mio | Power | Baterai | Need onsite_Tshooting Power, healthy check rectbatt plan 19-sep-26 | Rectifier & Battery System |  | Tshooting Power | Tshooting Power, healthy check rectbatt plan 19-sep-26 | W39 | High Effort | [7 empty] | 39 |  | OPEN
108 | KSN714 | KSN714_N3TTUMBANGMANANGEIDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 691192 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Propose upgrade SPS | List 10 site propose Upgrade SPS | TBD | Low Effort |  |  |  | 2026-10-11 |  |  |  | 41 |  | OPEN | 2026-10-11
109 | KSN715 | KSN715_N3TPENDANANGEDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) | W42 | High Effort | Medium Impact | OPEN | [5 empty] | 42 |  | OPEN | 2026-10-09
110 | KSN716 | KSN716_N3TTUMBANGGAEIDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) | W42 | High Effort | Medium Impact | OPEN | [5 empty] | 42 |  | OPEN | 2026-10-13
111 | KSN720 | KSN720_N3TPARUPUKDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) | W42 | High Effort | Medium Impact | DONE |  | 2026-10-07 | 2026-10-10 |  | done permbersihan panel | 42 | 41 | DONE | 2026-10-07 | 2026-10-10
112 | KSN721 | KSN721_N3TSELATBANINGDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  | Propose upgrade SPS | List 10 site propose Upgrade SPS | TBD | High Effort |  | DONE |  | 2026-10-14 | 2026-10-10 |  | done permbersihan panel | 42 | 41 | DONE | 2026-10-14 | 2026-10-10
113 | KSN722 | KSN722_N3TSEBANGAUJAYADMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY |  |  | Yes | Yes | 2 | 863990 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Propose upgrade SPS | List 10 site propose Upgrade SPS | TBD | Low Effort |  | DONE |  | 2026-10-12 | 2026-10-11 |  | done permbersihan panel | 42 | 41 | DONE | 2026-10-12 | 2026-10-11
114 | KSN765 | C_KSN765_TAWANGRANGASTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 2073576 | 2-3 Mio | Power | Baterai | PLN off > 3 jam, bbt site 3 jam_add 2P battery | Rectifier & Battery System |  | Add Battery 2p | add 2P battery | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Swap Battery |  |  |  | OPEN |  |  | Belum ada plan;
115 | KSN770 | KSN770_TUMBANGMARAKTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 1295985 | 1-2 Mio | Power | Baterai | Battery 2p OK, impact PLN Off > 3jam_add 2P battery | Rectifier & Battery System |  | Add Battery 2p | add 2P battery | W39 | High Effort | High Impact | OPEN |  |  |  | Refinement FO Telkom |  | 39 |  | OPEN
116 | MTW005 | MTW005_KM64PURUKCAHUDMT | NOP PALANGKARAYA | BRONZE | GENSET | BATTERY |  |  | Yes | Yes | 2 | 1209586 | 1-2 Mio | Power | Genset | Genset Broken | SPS Tsel Recovery |  |  |  |  | High Effort | [5 empty] | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
117 | MTW011 | C_MTW011_LUWEHULUDMT | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  |  | Yes |  | 1 | 1036788 | 1-2 Mio | Power | Rectifier | Upgrade battery 2P | Rectifier & Battery System |  | Add Battery 1p | Upgrade 1m1P | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
118 | MTW014 | MTW014_GUNUNGPUREI | NOP PALANGKARAYA | GOLD | PLN | PLN 12H |  | Yes |  |  | 1 | 1209586 | 1-2 Mio | Power | Baterai | PLN 12 jam, battery huawei 5P, anakan 2 site_upgrade 2P battery + rack slave / rect transmisi 3m 2P | Rectifier & Battery System |  | Escalate to PLN | upgrade 2P battery + rack slave / rect transmisi 3m 2P | TBD | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
119 | MTW015 | MTW015_LAHEI | NOP PALANGKARAYA | PLATINUM | PLN | GENSET |  | Yes |  |  | 1 | 2678369 | 2-3 Mio | Power | Genset | Need repair Genset ex MTW005_Repair Genset by SVA (assigned) /proses order material genset plan complete 30-sep | Genset Rectification |  | Genset Rectification | Repair Genset by SVA (assigned) /proses order material genset plan complete 30-sep | TBD | Low Effort |  |  |  | 2026-10-15 |  |  |  | 42 |  | OPEN
120 | MTW017 | MTW017_TUMPUNGLAUNG | NOP PALANGKARAYA | PLATINUM | PLN | PLN 12H + GENSET |  | Yes | Yes |  | 2 | 3110364 | > 3 Mio | Power | Baterai | PLN 12 jam, Battery only 2p, EnvaValid_upgrade 2P battery bts & Healty genset | Rectifier & Battery System |  | Add Battery 2p | upgrade 2P battery bts & Healty genset | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Swap Battery |  |  |  | OPEN |  |  | Belum ada plan;
121 | MTW018 | C_MTW018_SI_B2B_AGU_KANDAUTSEL | NOP PALANGKARAYA | BRONZE | CORPORATE | BATTERY | Yes |  |  | Yes | 2 | 691192 | < 1 Mio | Power | Corporate | Power Corporate Off | Rectifier & Battery System | Need Battery 3P |  |  |  | High Effort |  | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
122 | MTW024 | MTW024_TBKAMAWENTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1987177 | 1-2 Mio | Power | Baterai | Pemadaman PLN >3jam, BBT 1jam, 3P battery faulty_Swap battery 3P | Rectifier & Battery System |  | Add Battery 2p | Swap battery 3P | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
123 | MTW025 | C_MTW025_IAAS_AGU_PANDRANSCO | NOP PALANGKARAYA | BRONZE | CORPORATE | BATTERY |  |  | Yes |  | 1 | 259197 | < 1 Mio | Power | Rectifier | Escalation to TIF | Rectifier & Battery System |  |  |  |  | High Effort | [5 empty] | Refinement FO Telkom |  |  |  | OPEN |  |  | Belum ada plan;
124 | MTW032 | MTW032_IAAS_SMMSMESSBARITHOSCO | NOP PALANGKARAYA | PLATINUM | CORPORATE | BATTERY |  | Yes |  |  | 1 | 2073576 | 2-3 Mio | Power | Baterai | Power corporate battery 2P, impact PLN off FE (MTW061)_MTW061 4P battery transmisi, 2P faulty..need swap 2P | Rectifier & Battery System |  | Add Battery 2p | MTW061 4P battery transmisi, 2P faulty, need swap 2P | W45 | High Effort | High Impact | OPEN | [5 empty] | 45 |  | OPEN
125 | MTW033 | MTW033_BENAOTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 2419172 | 2-3 Mio | Power | Baterai | pemadaman massive pln | Rectifier & Battery System |  | Add Battery 2p | Add recty / upgrade battery, Sva assigned (waiting FNA asset approved/waiting RTPE approved | W45 | High Effort | High Impact | OPEN |  |  |  | Swap System |  | 45 |  | OPEN
126 | MTW034 | MTW034_LEMOTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  | Yes |  | 1 | 2073576 | 2-3 Mio | Power | Rectifier | Swap battery 2P | Rectifier & Battery System |  | Reroute link fading | Reroute link MTW034 _ MTW063 link ready/ waiting ISR released | TBD | High Effort | [5 empty] | Upgrade Module & Swap Battery |  |  |  | OPEN |  |  | Belum ada plan;
127 | MTW035 | MTW035_RIMBASARITBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 2159975 | 2-3 Mio | Transmisi | Impact Simpul | Impact Hub MTW005_done ts genset di MTW005 | Impact Hub |  | Impact Hub | done ts genset di MTW005 | W39 | Medium Effort |  | DONE | [5 empty] | 39 | 39 | DONE |  |  | DONE tanpa Date Actual;
128 | MTW060 | MTW060_RUJIPTI | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1987177 | 1-2 Mio | Power | Baterai | Pemadaman PLN >3jam, BBT 3jam_Battery 5p still OK, impact pemadaman | Rectifier & Battery System |  | Tshooting power | battery 5p still OK, impact pemadaman | W39 | High Effort | [7 empty] | 39 |  | OPEN
129 | MTW063 | MTW063_POLTEKMUARATEWEHPTI | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  |  | Yes | 1 | 1987177 | 1-2 Mio | Power | Rectifier | site flicker impact modul faulty | Troubleshooting IP Radio |  | Reroute link fading | Reroute link MTW034 _ MTW063 link ready/ waiting ISR released |  | Low Effort | [9 empty] | OPEN |  |  | Belum ada plan;
130 | MTW072 | MTW072_BATURAYADMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1814379 | 1-2 Mio | Power | Baterai | Pemadaman PLN >3jam, BBT 3jam_Done upgrade 1P battery BTS | Rectifier & Battery System |  | Add Battery 1p | Done upgrade 1P battery BTS | W39 | High Effort | High Impact | OPEN | [5 empty] | 39 |  | OPEN
131 | MTW169 | C_MTW169_MONTALLATTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 1814379 | 1-2 Mio | Power | Baterai | Pemadaman PLN >3jam, BBT 3jam_Battery 4p still OK, impact pemadaman | Rectifier & Battery System |  | Tshooting Power | Battery 4p still OK, impact pemadaman | W39 | High Effort | [5 empty] | Upgrade Module & Battery |  | 39 |  | OPEN
132 | MTW172 | MTW172_B2BPTMULTIPERSADAGATRAMEGAHSCO | NOP PALANGKARAYA | GOLD | CORPORATE | BATTERY |  | Yes | Yes |  | 2 | 1987177 | 1-2 Mio | Transmisi | Impact Simpul | Impact Simpul KKP065 down. PLN Undervoltage, propose genset | Impact Hub | Propose genset simpul Site KKP065 | Impact Hub | Add recty / upgrade battery di MTW003 |  | Medium Effort |  | OPEN |  | 2026-10-15 |  |  |  | 42 |  | OPEN
133 | MTW176 | MTW176_TAWANJAYADMT | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes |  |  | 1 | 1987177 | 1-2 Mio | Power | PLN Off | Kabel power kwh to acpdb short_Replace cable power | Perbaikan kabel |  | Replace cable power | Replace cable power | W45 | Low Effort |  |  |  | 2026-10-14 |  |  |  | 45 |  | OPEN
134 | MTW179 | MTW179_N3TSAMPIRANG2DMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 345596 | < 1 Mio | Power | Solar Cell | Pembersihan Panel, Butuh Pemangkasan Pohon.Open TOTI ke TP | PSB PLN | Pembersihan Panel, Butuh Pemangkasan Pohon.Open TOTI ke TP | New System Rectifier | PSB PLN On going by Verdanco |  | High Effort | [9 empty] | DONE
135 | MTW180 | MTW180_N3TBENANGIN3DMT | NOP PALANGKARAYA | BRONZE | PLN | SPS | Yes |  | Yes |  | 2 | 345596 | < 1 Mio | Power | Solar Cell | PSB Done, Waiting new system rectifier for hybrid | Hybrid PLN With SPS | PSB Done, Waiting new system rectifier for hybrid | New System Rectifier | PSB PLN Done, Not yet CO due to Rectifier not ready |  | Medium Effort |  |  |  | 2026-10-16 |  |  |  | 42 |  | OPEN
136 | NTH002 | NTH002_N3TPANTAILAGADMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 777591 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  | Upgrade SPS | Upgrade SPS on going by Biliton |  | High Effort |  | DONE |  | 2026-09-29 | 2026-09-29 |  | done permbersihan panel | 40 | 40 | DONE | 2026-09-29 | 2026-09-29
137 | NTH012 | N_NTH012_N3TBUNTUTLELENGDMT | NOP PALANGKARAYA | BRONZE | PLN | SPS |  |  | Yes |  | 1 | 863990 | < 1 Mio | Power | Solar Cell | PLN Done, Waiting team onsite hybrid PLN with SPS ¦ Done | Hybrid PLN With SPS | PLN Done, Waiting team onsite hybrid PLN with SPS ¦ Done |  |  |  | Medium Effort |  | DONE |  | 2026-09-02 | 2026-09-02 |  | Done co PLN | 36 | 36 | DONE
138 | NTH044 | NTH044_N3TTUMBANGPAKUDMT | NOP PALANGKARAYA | BRONZE | PLN | SPS |  |  | Yes |  | 1 | 691192 | < 1 Mio | Power | Solar Cell | Wiring Problem | SPS Tsel Recovery | Wiring Problem |  |  |  | High Effort |  | DONE |  | 2026-09-02 | 2026-09-02 |  | Done co PLN | 36 | 36 | DONE
139 | NTH045 | NTH045_N3TMUROIRAYADMT | NOP PALANGKARAYA | PLATINUM | SPS | GENSET |  |  | Yes | Yes | 2 | 1295985 | 1-2 Mio | Power | Solar Cell | Block Engine Genset Pecah ¦ Saat ini menggunakan MBP | Need Upgrade SPS & Perbaikan Genset | Block Engine Genset Pecah ¦ Saat ini menggunakan MBP | Tshooting Genset | perbaikan modul sps and timer genset plan 3-sep-26 | W39 | High Effort | Low Impact | ON GOING |  | 2026-10-01 | 2026-10-01 |  | Problem baru radiator mbp problem, done pembersihan sps | 39 | 40 | DONE |  |  | Ada Date Actual, status belum DONE; Reschedule (Date Plan > Week Target);
140 | NTH047 | NTH047_N3TTUMBANGMALAWANDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY |  |  | Yes |  | 1 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | High Effort | Medium Impact | DONE |  | 2026-10-07 | 2026-10-07 |  | done permbersihan panel | 41 | 41 | DONE
141 | NTH058 | NTH058_N3TSUNGAILOBANGDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes |  | 2 | 691192 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | High Effort | Medium Impact | DONE |  | 2026-10-03 | 2026-10-03 |  | done permbersihan panel | 40 | 40 | DONE | 2026-10-03 | 2026-10-03
142 | NTH065 | N_NTH065_N3TSEIPINANGDMT | NOP PALANGKARAYA | SILVER | PLN | SPS | Yes |  | Yes |  | 2 | 1382384 | 1-2 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | Low Effort |  | DONE |  | 2026-10-06 | 2026-10-06 |  | done visit dan pengambilan data sps ,site sudah full PLN 24 jam | 41 | 41 | DONE
143 | NTH070 | NTH070_N3TTUMBANGNUSADMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  |  |  |  | High Effort | [9 empty] | OPEN | 2026-10-13 |  | Belum ada plan;
144 | NTH071 | NTH071_N3TTUMBANGKATAEIDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY |  |  | Yes | Yes | 2 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | High Effort | Medium Impact | OPEN | [7 empty] | OPEN | 2026-10-10 |  | Belum ada plan;
145 | NTH073 | NTH073_N3TTUMBANGTUNDUDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 518394 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | High Effort | Medium Impact | OPEN | [7 empty] | OPEN | 2026-10-16 |  | Belum ada plan;
146 | NTH074 | NTH074_N3TTUMBANGTAEIDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 691192 | < 1 Mio | Power | Solar Cell | PV Faulty 12 Unit | SPS Tsel Recovery | Check on site done 12-Sept 26. Finding PV Faulty 12 Unit, propose claim daisy | Propose upgrade SPS | List 10 site propose Upgrade SPS |  | High Effort | [9 empty] | DONE | 2026-09-15 | 2026-09-15
147 | NTH075 | N_NTH075_N3TTUMBANGTIHISDMT | NOP PALANGKARAYA | SILVER | SPS | BATTERY |  |  | Yes | Yes | 2 | 863990 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  |  |  |  | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
148 | NTH076 | NTH076_N3TTUMBANGMANDUREIDMT | NOP PALANGKARAYA | BRONZE | PLN | SPS | Yes |  | Yes |  | 2 | 863990 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) | TBD | High Effort | Medium Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
149 | NTH079 | N_NTH079_N3TMUARAPARIDMT | NOP PALANGKARAYA | BRONZE | PLN | BATTERY |  |  | Yes |  | 1 | 1036788 | 1-2 Mio | Power | Rectifier | upgrade 2P battry with rack slave or add new recty | Rectifier & Battery System |  |  |  |  | High Effort | [5 empty] | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
150 | NTH080 | N_NTH080_N3TMANISDMT | NOP PALANGKARAYA | SILVER | SPS | GENSET |  |  | Yes | Yes | 2 | 863990 | < 1 Mio | Power | Solar Cell | Radiator problem | Need Upgrade SPS & Perbaikan Genset | Radiator problem |  |  |  | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
151 | NTH081 | NTH081_N3TTUMBANGDIRINGDMT | NOP PALANGKARAYA | BRONZE | PLN | SPS | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Battery Faulty | SPS Tsel Recovery | Battery Faulty |  |  |  | High Effort | [5 empty] | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
152 | NTH082 | N_NTH082_N3TBARUNANG2DMT | NOP PALANGKARAYA | BRONZE | PLN | SPS |  |  | Yes |  | 1 | 691192 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | High Effort | Medium Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
153 | NTH083 | N_NTH083_N3TTUMBANGMANGKETAIDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 691192 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  | Propose upgrade SPS |  | TBD | High Effort | [9 empty] | OPEN | 2026-10-17 |  | Belum ada plan;
154 | NTH085 | NTH085_N3TDANDANGDMT | NOP PALANGKARAYA | SILVER | PLN | SPS | Yes |  | Yes |  | 2 | 863990 | < 1 Mio | Power | Solar Cell | Penggantian kabel power hybrid PLN & SPS ¦ Done | Hybrid PLN With SPS | Penggantian kabel power hybrid PLN & SPS ¦ Done |  |  |  | Medium Effort |  | DONE |  | 2026-08-25 | 2026-08-25 | PSB PLN | Done add kabel | 35 | 35 | DONE
155 | NTH086 | NTH086_N3TSEIBAKAUDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes |  | 2 | 691192 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Propose upgrade SPS | List 10 site propose Upgrade SPS | TBD | Low Effort |  | DONE |  | 2026-10-10 | 2026-10-10 |  | Sudah dilakukan pembersihan SPS | 41 | 41 | DONE | 2026-10-19 | 2026-10-10
156 | NTH088 | N_NTH088_N3TSUBURINDAHDMT | NOP PALANGKARAYA | BRONZE | PLN | BATTERY | Yes |  |  |  | 1 | 1814379 | 1-2 Mio | Power | Rectifier | Suspect Rectifier Module | Replace Module | Replace Module APR faulty | Replace Module | Need replace modul recty faulty, avail already OK | Close | Medium Effort | Medium Impact | DONE |  | 2026-09-07 | 2026-09-07 |  | done onkan module | 37 | 37 | DONE
157 | NTH112 | NTH112_N3TGERAGUDMT | NOP PALANGKARAYA | BRONZE | SPS | GENSET | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Water pump problem | Need Upgrade SPS & Perbaikan Genset | Water pump problem | Pergantian water pump |  | TBD | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
158 | NTH114 | NTH114_N3TDEHESDMT | NOP PALANGKARAYA | BRONZE | PLN MULTIGUNA | SPS |  |  | Yes |  | 1 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) | W42 | High Effort | Medium Impact | OPEN | [5 empty] | 42 |  | OPEN
159 | NTH119 | NTH119_N3TMALUNGAIDMT | NOP PALANGKARAYA | BRONZE | PLN | BATTERY |  |  | Yes |  | 1 | 1295985 | 1-2 Mio | Power | Rectifier | add battery 2P | Rectifier & Battery System |  |  |  |  | High Effort | [5 empty] | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
160 | NTH120 | NTH120_N3TMANGKAWUKDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 777591 | < 1 Mio | Power | Solar Cell | PV Faulty 2 Unit | PSB PLN | PV Faulty 2 Unit | New Rectifier | List 10 site propose Upgrade SPS | W39 | High Effort |  | DONE |  | 2026-10-02 | 2026-10-02 |  | Done CO best Affort Tim KUT untuk modif Rectifier temporary | 39 | 40 | DONE |  |  | Reschedule (Date Plan > Week Target);
161 | NTH121 | N_NTH121_N3TBETANGNALONGDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes |  | 2 | 777591 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  | PSB PLN |  |  | High Effort | [9 empty] | OPEN | 2026-10-16 |  | Belum ada plan;
162 | NTH125 | N_NTH125_N3TTARUSANDMT | NOP PALANGKARAYA | SILVER | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  | Propose upgrade SPS | List 10 site propose Upgrade SPS | TBD | High Effort | [9 empty] | OPEN | 2026-10-17 |  | Belum ada plan;
163 | NTH129 | N_NTH129_N3TPANAENDMT | NOP PALANGKARAYA | BRONZE | PLN | BATTERY |  |  | Yes |  | 1 | 1468783 | 1-2 Mio | Power | Rectifier | upgrade battery 2P | Upgrade PLN |  | Upgrade battery 2P & Upgrade PLN |  | TBD | High Effort | Low Impact | OPEN |  |  |  | Upgrade Daya PLN & Battery |  |  |  | OPEN |  |  | Belum ada plan;
164 | NTH141 | N_NTH141_N3TTUMBANGKABAYANDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY |  |  | Yes | Yes | 2 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) | W43 | High Effort | Medium Impact | OPEN | [5 empty] | 43 |  | OPEN | 2026-10-15
165 | NTH144 | NTH144_N3TTUMBANGRUNENDMT | NOP PALANGKARAYA | SILVER | PLN | SPS |  |  | Yes |  | 1 | 863990 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Need check on site | PSB PLN Done, Rectifier done 3M3P ZTE Hitam | W43 | Low Effort |  |  |  | 2026-10-15 |  |  |  | 43 |  | OPEN
166 | NTH153 | N_NTH153_N3TSEIGITADMT | NOP PALANGKARAYA | GOLD | SPS | BATTERY |  |  | Yes | Yes | 2 | 863990 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS | Tshooting power, Healty chek battery sps plan 7-sep-26 (done) | Propose upgrade SPS | List 10 site propose Upgrade SPS | W39 | High Effort |  | DONE |  | 2026-10-02 | 2026-10-03 |  | done permbersihan panel,kendala hanya di asap sudah di trial baterai masih kuat backup 24jam dengan kondisi load saat ini | 39 | 40 | DONE | 2026-10-03 | 2026-10-03 | Reschedule (Date Plan > Week Target);
167 | NTH154 | NTH154_N3TRANGANBURIHDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 863990 | < 1 Mio | Power | Solar Cell | Fauly Battery 1 Pack (disconnect done) | Need Upgrade SPS | Fauly Battery 1 Pack (disconnect done) | Claim daisy panel pv | Total 22 panel bersih, 1 Panel PV broken | TBD | Medium Effort | Low Impact | DONE |  | 2026-09-18 | 2026-09-18 |  | done pembersihan panel dan baterai 1 faulty sudah dilepas | 38 | 38 | DONE | 2026-10-28
168 | NTH157 | NTH157_N3TJAKATANPARIDMT | NOP PALANGKARAYA | SILVER | SPS | BATTERY |  |  | Yes | Yes | 2 | 863990 | < 1 Mio | Power | Solar Cell | Solar cell not Maximum Supply Equipment | Need Upgrade SPS |  | Propose upgrade SPS |  | TBD | High Effort |  | DONE |  | 2026-10-20 | 2026-10-07 |  | done permbersihan panel | 43 | 41 | DONE | 2026-10-20 | 2026-10-07
169 | NTH159 | N_NTH159_N3TBARUNANGDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY |  |  | Yes | Yes | 2 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | High Effort | Medium Impact | OPEN | [7 empty] | OPEN | 2026-10-17 |  | Belum ada plan;
170 | NTH160 | N_NTH160_N3TBINAJAYADMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY |  |  | Yes | Yes | 2 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | High Effort | Medium Impact | OPEN | [7 empty] | OPEN | 2026-10-22 |  | Belum ada plan;
171 | NTH245 | C_NTH245_N3TTANJUNGJAWADMT | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  |  | Yes |  | 1 | 1209586 | 1-2 Mio | Power | Rectifier | Upgrade daya PL & upgrade battery 2P | Rectifier & Battery System |  | need Upgrade battery 2P & Upgrade PLN |  | TBD | High Effort | [5 empty] | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
172 | NTH246 | C_NTH246_BERENGMALAKADMT | NOP PALANGKARAYA | BRONZE | PLN | BATTERY | Yes |  |  | Yes | 2 | 345596 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Propose upgrade SPS | List 10 site propose Upgrade SPS | TBD | Low Effort |  |  |  | 2026-10-04 |  | Refinement FO Telkom |  | 40 |  | OPEN
173 | NTH248 | NTH248_N3TBERENGBARUDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1468783 | 1-2 Mio | Power | Baterai | PLN OFF > 3 JAM BBT 1 JAM | Rectifier & Battery System |  | Add Battery 2p | add 2P battery | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
174 | NTH249 | NTH249_N3TLUWUKLANGKUASDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1295985 | 1-2 Mio | Power | Genset | PLN OFF > 3 JAM BBT 2 JAM | Genset Rectification |  | Add Battery 2p | Swap batt 2P, claim battery 2p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
175 | NTH250 | NTH250_N3TTUYUNDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 1814379 | 1-2 Mio | Power | PLN Off | Upgrade daya PLN 4400VA to 13200VA, Battrey 2p Nok, claim battery warranty | Rectifier & Battery System |  | Add Battery 2p | claim battrey 2p | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
176 | NTH261 | C_NTH261_N3T_MANGKAHUIDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  | Yes |  | 1 | 1295985 | 1-2 Mio | Power | Rectifier | Escalation to TIF | Rectifier & Battery System |  | Add Battery 2p |  | TBD | High Effort | High Impact | OPEN |  |  |  | Refinement FO Telkom |  |  |  | OPEN |  |  | Belum ada plan;
177 | PLK005 | C_PLK005_PETUKBARUNAIDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  | Yes |  | 1 | 1209586 | 1-2 Mio | Power | Rectifier | Upgrade battery 2p | Rectifier & Battery System |  | Add Battery 2p | add 2P battery | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
178 | PLK025 | PLK025_AddSect_TANGKILING | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  |  | Yes |  | 1 | 1900778 | 1-2 Mio | Power | Rectifier | Swap 3p battery with litium | Rectifier & Battery System |  | Add Battery 2p | swap battrey 3p | W39 | High Effort | Medium Impact | OPEN |  |  |  | Swap System |  | 39 |  | OPEN
179 | PLK839 | PLK839_N3TMUNGKUBARUDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  | Yes | Yes | 2 | 1987177 | 1-2 Mio | Power | Rectifier | Escalation to TIF | Rectifier & Battery System |  | Add Battery 2p | Perbaikan enva , swap battery 2p | W41 | High Effort | High Impact | OPEN |  |  |  | Refinement FO Telkom |  | 41 |  | OPEN
180 | PPS005 | PPS005_KARYALUHURSEJATITBG | NOP PALANGKARAYA | PLATINUM | CORPORATE | BATTERY |  | Yes |  |  | 1 | 2332773 | 2-3 Mio | Transmisi | FO Telkom Putus | Aktivitas Pihak ke-3 | FO Cut Escalation |  | Tshooting Power | Perbaikan enva | W40 | High Effort |  | DONE |  | 2026-09-30 | 2026-09-30 |  | Baterai 2 faulty CSU faulty | 40 | 40 | DONE
181 | PPS019 | N_PPS019_DANDANGTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  |  | Yes | 1 | 950389 | < 1 Mio | PLN | PLN Off | Under investigate | Rectifier & Battery System | Add Battery | Add Battery | Add Battery 2p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
182 | PPS023 | PPS023_GANDANG | NOP PALANGKARAYA | GOLD | PLN | GENSET |  | Yes | Yes | Yes | 3 | 2246374 | 2-3 Mio | Power | Baterai | improve ACTION DONE_Upgrade Module & Battery | Rectifier & Battery System |  | Add Battery 2p | PLN Off >3 jam. Battery 2p OK, 1p Faulty (done claim battery, waiting deliver) | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
183 | PPS026 | PPS026_SUKAJADIDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1641581 | 1-2 Mio | Power | Baterai | 2p battrey nok_swap batt 2P claim battrey | Rectifier & Battery System |  | Add Battery 2p | swap batt 2P claim battrey | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
184 | PPS027 | PPS027_NUSAINDAHDMT | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 1900778 | 1-2 Mio | Power | Baterai | battrey 3b nok_Swap batt 2P | Rectifier & Battery System |  | Add Battery 2p | Swap batt 2P | TBD | High Effort | Medium Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
185 | PPS029 | PPS029_LAWANGURUDMT | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes |  |  | 1 | 2419172 | 2-3 Mio | Power | Baterai | Sc200 faulty 2 pcs, 2p battery faulty_replace sc200 and swap Battery | Rectifier & Battery System |  | Replace Sc200 | replace sc200 and swap Battery |  | High Effort | [9 empty] | OPEN |  |  | Belum ada plan;
186 | PPS065 | PPS065_SEBANGAUKUALA | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 2591970 | 2-3 Mio | Power | Baterai | 1p nok dari 6p_claim warannty 1p | Rectifier & Battery System |  | Warranty Battery claim | claim warannty 1p | TBD | High Effort | High Impact | [8 empty] | OPEN |  |  | Belum ada plan;
187 | PPS077 | PPS077_PAHAWANPTI | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes |  |  | 1 | 2591970 | 2-3 Mio | Power | Baterai | Battery stolen_Add 2p battery (exercise donor) | Rectifier & Battery System |  | Add Battery 2p | Add 2p battery (exercise donor) |  | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
188 | PPS084 | PPS084_PTSCP2DMT | NOP PALANGKARAYA | PLATINUM | CORPORATE | BATTERY |  | Yes |  | Yes | 2 | 3196763 | > 3 Mio | Radio | Cell down | Troubleshooting | Celldown | REPLACE RRU | Add Battery 1p | Rebalancing load ,ambil data log, claim battery 1p | W39 | High Effort | High Impact | DONE |  | 2026-09-30 | 2026-09-30 |  | done bcp | 39 | 40 | DONE |  |  | Reschedule (Date Plan > Week Target);
189 | PPS094 | PPS094_TUMBANGDANAUDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 1641581 | 1-2 Mio | Power | Baterai | 4p nok iob dan lvd nok_claim battrey 4p replace iob dan lvd | Rectifier & Battery System |  | Add Battery 2p | claim battrey 4p replace iob dan lvd | TBD | High Effort | High Impact | OPEN |  |  |  | Rektifikasi Rectifer |  |  |  | OPEN |  |  | Belum ada plan;
190 | PPS102 | PPS102_TALIOHULUPTI | NOP PALANGKARAYA | BRONZE | PLN | BATTERY |  |  |  | Yes | 1 | 1727980 | 1-2 Mio | Power | PLN Off | Under investigate | Rectifier & Battery System | Add Battery | Add Battery | Add Battery 2p | TBD | High Effort | Low Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
191 | PPS108 | PPS108_BARUNAIPTI | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 2591970 | 2-3 Mio | Power | Baterai | 1P battrey NOK_claim battrey 1P | Rectifier & Battery System |  | Add Battery 1p | claim battrey 1P | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
192 | PPS111 | PPS111_SAKTIMAITJAYADMT | NOP PALANGKARAYA | BRONZE | CORPORATE | BATTERY | Yes |  | Yes |  | 2 | 1987177 | 1-2 Mio | Power | Corporate | Power Corporate Off | Eskalasi Listrik Corporate | Corporate escalation |  |  |  | Medium Effort |  | OPEN |  |  |  | Power Corporate | Perlu add battery |  |  | OPEN |  |  | Belum ada plan;
193 | PPS131 | PPS131_TAHAIJAYADMT | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 2419172 | 2-3 Mio | Power | Baterai | battrey 1p nok dari 5P_claim battrey 1p,swap battery 1p | Rectifier & Battery System |  | Add Battery 1p | claim battrey 1p,swap battery 1p | TBD | High Effort | Medium Impact | OPEN |  |  |  | Rektifikasi Rectifer |  |  |  | OPEN |  |  | Belum ada plan;
194 | PPS134 | N_PPS134_PARAHANGANDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1987177 | 1-2 Mio | Power | Baterai | Battery 3p faulty_Claim Battery 3p | Rectifier & Battery System |  | Add Battery 2p | Claim Battery 3p |  | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
195 | PPS137 | N_PPS137_DSPAMARUNANDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1814379 | 1-2 Mio | Power | Baterai | Battery 2p faulty_Claim Battery 2p | Rectifier & Battery System |  | Add Battery 2p | Claim Battery 2p |  | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
196 | PPS139 | PPS139_DESASIGIPTI | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 1641581 | 1-2 Mio | Power | Baterai | Sc200 faulty, Battery floating VRLA 4b_Request SC200, Swap Battery 4p | Rectifier & Battery System |  | Add Battery 2p | Request SC200, Swap Battery 4p | W44 | High Effort | High Impact | OPEN | [5 empty] | 44 |  | OPEN
197 | PPS222 | PPS222_DSGARANTUNGCMI | NOP PALANGKARAYA | BRONZE | PLN | BATTERY |  |  |  | Yes | 1 | 1209586 | 1-2 Mio | Power | PLN Off | Under investigate | Rectifier & Battery System | Add Battery | Add Battery | Add Battery 2p | TBD | High Effort | Low Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
198 | PPS235 | PPS235_DESAHANUABANAMADMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes |  |  | 1 | 2246374 | 2-3 Mio | Power | Baterai | •SC200 NOK _Request SC200 done, waiting process delivery part | Rectifier & Battery System |  | Tshooting Power | Request SC200 done, waiting process delivery part | W44 | High Effort | [7 empty] | 44 |  | OPEN
199 | PPS250 | PPS250_KARYALUHURSEJATITBG | NOP PALANGKARAYA | GOLD | CORPORATE | BATTERY |  | Yes |  |  | 1 | 2678369 | 2-3 Mio | Power | Corporate | Power Corporate Off | Rectifier & Battery System | Swap Battery 0M4P | Add Battery 2p | claim battrey 3p,swap battery 3p | TBD | High Effort | High Impact | OPEN | [7 empty] | OPEN |  |  | Belum ada plan;
200 | PPS264 | PPS264_N3TTAMBAKDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 1900778 | 1-2 Mio | Power | Baterai | Battery 3P, 1P active, 2P deactivated, Upgrade PLN done, FU battery activation | Rectifier & Battery System |  | Upgrade Daya | Upgrade daya | TBD | High Effort | [5 empty] | Upgrade Daya PLN |  |  |  | OPEN |  |  | Belum ada plan;
201 | PPS277 | PPS277_PTSURYAMASTBG | NOP PALANGKARAYA | PLATINUM | CORPORATE | BATTERY |  | Yes |  |  | 1 | 3023965 | > 3 Mio | Transmisi | Impact Simpul | IMPACT SITE HUB PPS065 PLN Undervoltaget | Impact Hub | Propose genset simpul Site KKP065 | Impact Hub | Perbaikan enva, impact hub , power corporate escalation | W39 | Medium Effort |  | DONE |  | 2026-09-29 | 2026-09-29 |  | Baterai aman, enva tidak bisa valid karena rusak di soket BTS | 39 | 40 | DONE |  |  | Reschedule (Date Plan > Week Target);
202 | PRC002 | PRC002_MUARALAUNGITBG | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes | Yes |  | 2 | 3196763 | > 3 Mio | Power | Baterai | CSU faulty, Battery 4p faulty_Replace csu (proses Rekuest), swap battery, claim battery | Rectifier & Battery System |  | Add Battery 4p | Replace csu (proses Rekuest), swap battery, claim battery | TBD | High Effort | High Impact | OPEN |  |  |  | Refinement FO Telkom |  |  |  | OPEN |  |  | Belum ada plan;
203 | PRC004 | PRC004_TUMBANGLAHUTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 1555182 | 1-2 Mio | Power | Baterai | Pemadaman PLN > 3jam, Battery 2P only still back up_Upgrade battery 2P | Rectifier & Battery System |  | Add Battery 2p | Upgrade battery 2P | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
204 | PRC006 | PRC006_MARUNDA | NOP PALANGKARAYA | SILVER | GENSET | BATTERY |  |  | Yes |  | 1 | 3196763 | > 3 Mio | Power | Genset | GENSET TSEL | Genset Rectification |  | BBM Readyness | Split rectifier untuk BTS dan Transmisi (done), Add battery 8p (done), Perbaikan genset (done) |  | Low Effort |  | DONE |  | 2026-08-19 | 2026-08-19 |  | Done add accu,add bc,dan autonisasi genset | 34 | 34 | DONE
205 | PRC016 | C_PRC016_B2BHARMONIPANCAUTAMASITESABSCO | NOP PALANGKARAYA | SILVER | PLN | BATTERY |  |  | Yes |  | 1 | 950389 | < 1 Mio | Power | Rectifier | Upgrade battery 2P | Rectifier & Battery System |  | Add Battery 2p | Battery not backup | TBD | High Effort | Medium Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
206 | PRC017 | PRC017_DIRUNGLINGKIN | NOP PALANGKARAYA | PLATINUM | PLN | GENSET |  | Yes |  |  | 1 | 3196763 | > 3 Mio | Power | Baterai | Battery faulty 5p and genset manual by pjs_Add 2P battery done, need automasi genset and education pjs, claim battery 5p | Rectifier & Battery System |  | Add Battery 2p | Add 2P battery done, need automasi genset and education pjs, claim battery 5p | W39 | High Effort | High Impact | OPEN | [5 empty] | 39 |  | OPEN
207 | PRC018 | PRC018_TUMBANGKUNYI | NOP PALANGKARAYA | GOLD | SPS TP | BATTERY | Yes |  | Yes |  | 2 | 2073576 | 2-3 Mio | Power | Solar Cell | SPS TP DMT Module Problem | SPS TP Improvement |  | Escalate TP | Genset stanby support inverter sps tp while drop | TBD | Medium Effort |  |  |  | 2026-10-14 |  |  |  | 42 |  | OPEN
208 | PRC024 | PRC024_MUARAUTUTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes | Yes | 3 | 2073576 | 2-3 Mio | Power | Baterai | Pemadaman PLN > 3jam, Battery 2p not back up, Enva revalidation_Helathy check battery, enva simulation | Rectifier & Battery System |  | Add Battery 2p | Helathy check battery, enva simulation | TBD | High Effort | High Impact | OPEN |  |  |  | Swap Rectifier & Upgrade Battery |  |  |  | OPEN |  |  | Belum ada plan;
209 | PRC025 | PRC025_TUMBANGMASAODMT | NOP PALANGKARAYA | GOLD | SPS TP | BATTERY |  |  | Yes |  | 1 | 1987177 | 1-2 Mio | Power | Solar Cell | SPS broken | SPS TP Improvement |  | Add Genset | SPS TP DMT, propose genset backup power | TBD | Medium Effort | [6 empty] | Under TP |  |  | OPEN |  |  | Belum ada plan;
210 | PRC026 | PRC026_BABUATDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  |  | Yes | 1 | 1814379 | 1-2 Mio | PLN | PLN Off | Under investigate | Impact Hub |  | Impact Hub | Impact SPS TP PRC025 |  | Medium Effort | [6 empty] | Impact SPS TP |  |  | OPEN |  |  | Belum ada plan;
211 | PRC051 | PRC051_DESABAHITOM | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  | Yes | Yes | 2 | 1814379 | 1-2 Mio | Power | Rectifier | Swap 2 Bank battery VRLA | Rectifier & Battery System |  | Add Battery 2p | Swap 2P battery + rack slave | TBD | High Effort | High Impact | OPEN |  |  |  | Swap System |  |  |  | OPEN |  |  | Belum ada plan;
212 | PRC138 | PRC138_HARMONIPANCAUTAMATBG | NOP PALANGKARAYA | BRONZE | PLN | BATTERY |  |  | Yes |  | 1 | 2073576 | 2-3 Mio | Power | Corporate | Power Corporate Off | Eskalasi Listrik Corporate | Corporate escalation | Troubleshooting | Propose dilakukan PM untuk pengecekkan issue di site |  | Medium Effort | Medium Impact | OPEN |  |  |  | Power Corporate | Waiting permit corporate |  |  | OPEN |  |  | Belum ada plan;
213 | PRC166 | PRC166_DESAKONUTDMT | NOP PALANGKARAYA | PLATINUM | PLN | BATTERY |  | Yes | Yes |  | 2 | 2505571 | 2-3 Mio | Power | Baterai | Battery 2p faulty, impact fo cut repeated_Swap 2P battery, claim battery 2p | Rectifier & Battery System |  | Add Battery 2p | Swap 2P battery, claim battery 2p | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
214 | PRC182 | C_PRC182_PTAKT | NOP PALANGKARAYA | BRONZE | CORPORATE | BATTERY |  |  |  | Yes | 1 | 1814379 | 1-2 Mio | Power | Corporate | Power Corporate Off | Eskalasi Listrik Corporate | Corporate escalation | Escalate to corporate | power issue corporate/lock down case internal corporate |  | Medium Effort |  | OPEN |  |  |  | Refinement FO Telkom | Waiting permit corporate |  |  | OPEN |  |  | Belum ada plan;
215 | PRC189 | PRC189_N3TKALANGDOHONGDMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 777591 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | High Effort | Medium Impact | OPEN | [7 empty] | OPEN | 2026-10-08 |  | Belum ada plan;
216 | PRC191 | N_PRC191_N3TTELOKJOLODMT | NOP PALANGKARAYA | BRONZE | SPS | BATTERY | Yes |  | Yes | Yes | 3 | 691192 | < 1 Mio | Power | Solar Cell | Need Visit On site | Need Visit On site | Need Visit On site TS SPS | Troubleshoot SPS | SPS Tsel need visit and claim daisy (part faulty) |  | High Effort | Medium Impact | OPEN | [7 empty] | OPEN | 2026-10-14 |  | Belum ada plan;
217 | PRC224 | PRC224_PTSAPTAINDRASEJATISCO | NOP PALANGKARAYA | GOLD | CORPORATE | BATTERY | Yes |  | Yes |  | 2 | 950389 | < 1 Mio | Power | Corporate | Power Corporate Off | Eskalasi Listrik Corporate | Corporate escalation | Escalate to corporate | escalate to B2B |  | Medium Effort |  | OPEN |  |  |  | Power Corporate | Waiting permit corporate |  |  | OPEN |  |  | Belum ada plan;
218 | PRC225 | N_PRC225_ISLAMICCENTERPRCTBG | NOP PALANGKARAYA | DIAMOND | PLN | BATTERY |  | Yes | Yes |  | 2 | 2764768 | 2-3 Mio | Power | Baterai | Battery faulty 2p_Swap battery 2p, claim battery 2p | Rectifier & Battery System |  | Add Battery 2p | Swap battery 2p, claim battery 2p | W39 | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  | 39 |  | OPEN
219 | PRC226 | PRC226_MUARABAKANONTBG | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  | Yes | Yes |  | 2 | 2073576 | 2-3 Mio | Power | Baterai | Battery 2P faulty, BBT 1 jam PLN Off >3jam_Swap 2P battery | Rectifier & Battery System |  | Add Battery 2p | Swap 2P battery | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Module & Battery |  |  |  | OPEN |  |  | Belum ada plan;
220 | TML010 | TML010_MRPLANTAUDMT | NOP PALANGKARAYA | BRONZE | PLN | BATTERY |  |  | Yes |  | 1 | 1641581 | 1-2 Mio | Power | Genset | add new genset site TML032 | Swap Genset Tsel |  | Impacted Hub | Impact site TML032, propose add 2p battery (SVA waiting approval) | W40 | High Effort | [7 empty] | 40 |  | OPEN
221 | TML032 | TML032_SGRARAWA | NOP PALANGKARAYA | SILVER | PLN | PLN 12H |  | Yes | Yes |  | 2 | 2073576 | 2-3 Mio | Power | Genset | PLN 12 jam, PLN sedang menghemat bbm pembangkit_Plan new genset by verdanco | Genset Rectification |  | Add Battery 2p | Rectifier Module Hariff Back Up Battery 12 Bank, ZTE ZXDC48 FB100C1 3 bank faulty | W45 | High Effort | Medium Impact | OPEN |  |  |  | Swap Genset Tsel |  | 45 |  | OPEN
222 | TML055 | TML055_DESABAMBANDMT | NOP PALANGKARAYA | BRONZE | PLN | BATTERY |  |  | Yes |  | 1 | 1295985 | 1-2 Mio | Power | Rectifier | Swap 2 Bank battery VRLA | Rectifier & Battery System |  | Add Battery 2p | Propose add battery lithium 2p (existing VRLA) | TBD | High Effort | Low Impact | OPEN |  |  |  | Swap System |  |  |  | OPEN |  |  | Belum ada plan;
223 | TML127 | TML127_ISATTELANGBARUDMT | NOP PALANGKARAYA | GOLD | PLN | BATTERY |  |  |  | Yes | 1 | 2332773 | 2-3 Mio | Power | Baterai | Escalation to Adaro | Rectifier & Battery System |  | Add Battery 2p | Upgrade 2P battery + rack slave | TBD | High Effort | High Impact | OPEN |  |  |  | Upgrade Battery |  |  |  | OPEN |  |  | Belum ada plan;
Formulas:
Plan Week (baseline) = IF([SITEID]="","",IF(LEFT([Week Target],1)="W",VALUE(MID([Week Target],2,2)),IF(ISNUMBER([Date Plan]),ISOWEEKNUM([Date Plan]),IF(ISNUMBER([Date Actual]),ISOWEEKNUM([Date Actual]),""))))
Actual Week = IF([Status Final]<>"DONE","",IF(ISNUMBER([Date Actual]),ISOWEEKNUM([Date Actual]),[Plan Week (baseline)]))
Plan Visit SPS = IF([SITEID]="","",IFERROR(IF(INDEX('Jadwal Visit SPS'!$AC5:AC305,MATCH([SITEID],'Jadwal Visit SPS'!$B5:B305,0))="","",INDEX('Jadwal Visit SPS'!$AC5:AC305,MATCH([SITEID],'Jadwal Visit SPS'!$B5:B305,0))),""))
Actual Visit SPS = IF([SITEID]="","",IFERROR(IF(INDEX('Jadwal Visit SPS'!$AD5:AD305,MATCH([SITEID],'Jadwal Visit SPS'!$B5:B305,0))="","",INDEX('Jadwal Visit SPS'!$AD5:AD305,MATCH([SITEID],'Jadwal Visit SPS'!$B5:B305,0))),""))
Note on AE4: Week Target (Wxx) jika diisi; jika TBD/kosong pakai ISO week dari Date Plan; jika belum ada plan tapi sudah ada Date Actual, pakai minggu Date Actual.
Note on AF4: ISO week dari Date Actual. Jika DONE tanpa Date Actual, dipakai Plan Week.
Note on AG4: DONE jika Action Status = DONE, Week Target = Close, atau Date Actual terisi. Selain itu ON GOING / OPEN.

## Jadwal Visit SPS
JADWAL VISIT SITE SPS TSEL — NOP PALANGKARAYA
Sumber: JADWAL VISIT SPS TSEL Kalimantan (Sheet1), khusus NOP Palangkaraya. Isi Plan Date (kolom AC) & Actual Date (kolom AD); kolom biru muda AF–AI otomatis.
No | SITEID | SITE NAME | NOP | DEPARTEMEN | SITE CLASS | Jumlah Site Anakan | Site Simpul | Site Backbone | Site BCP | Site Controller | NE Telkom | Radio | Long | Lat | Tower Owner | Tower Type | OA Site Date | Main Power | Backup Power | Action Plan | AVA Average (%) | Load (W) | Remark Load | Check PSB | Availability Agustus | Repetitive | Program H2 Area | Plan Date Site Visit | Actual Date Visit | Remark | Plan Date (baseline) | Status Visit | Ada di Tracker? | Status Improvement
1 | KSN720 | KSN720_N3TPARUPUKDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 113.3598 | -2.4171 | PT. Daya Mitra Telekomunikasi | SST | 2022-05-30 | SPS | BATTERY | Need SPS Recovery | 65.0567 | 1496.05 | >80% |  | Not Achieve | P1 | Upgrade SPS Tsel by Relokasi SPS | 2026-10-07 | 2026-10-10 |  | 2026-10-07 | Done | Ya | DONE
2 | NTH058 | NTH058_N3TSUNGAILOBANGDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 114.233 | -0.69238 | PT. Daya Mitra Telekomunikasi | SST | 2023-01-08 | SPS | BATTERY | Need SPS Recovery | 42.42 | 1320.019 | >80% |  | Not Achieve | P1 |  | 2026-10-03 | 2026-10-03 |  | 2026-10-03 | Done | Ya | DONE
3 | PRC189 | PRC189_N3TKALANGDOHONGDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 114.6352 | -0.33132 | PT. Daya Mitra Telekomunikasi | SST | 2023-02-06 | SPS | BATTERY | Need SPS Recovery | 56.88 | 1425.219 | >80% |  | Not Achieve | P1 | Rectification SPS Tsel | 2026-10-08 |  |  | 2026-10-08 | Overdue | Ya | OPEN
4 | KSN188 | KSN188_N3TTUMBANGLAMBI | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | GSM+L900 | 112.6072 | -1.1381 | PT. Daya Mitra Telekomunikasi | SST | 2022-06-25 | SPS | BATTERY | Need SPS Recovery | 41.01 | 758.048 | OK |  | Not Achieve | P1 | Rectification SPS Tsel | 2026-10-03 |  |  | 2026-10-03 | Overdue | Ya | OPEN
5 | KSN722 | KSN722_N3TSEBANGAUJAYADMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 113.6095 | -3.0627 | PT. Daya Mitra Telekomunikasi | SST | 2022-07-25 | SPS | BATTERY | Need SPS Recovery | 74.35 | 1244.22 | >80% |  | Not Achieve | P3 | Rectification SPS Tsel | 2026-10-12 | 2026-10-11 |  | 2026-10-12 | Done | Ya | DONE
6 | KKP306 | KKP306_N3TTUMBANGMANGKUTUPDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+L1800+L2100 | 114.3938 | -2.189 | PT. Daya Mitra Telekomunikasi | SST | 2022-04-16 | SPS | BATTERY | Need SPS Recovery | 68.39 | 1141.773 | OK |  | Not Achieve | P2 | Rectification SPS Tsel | 2026-10-10 |  |  | 2026-10-10 | Overdue | Ya | OPEN
7 | KSN193 | KSN193_N3TRANGANBAHEKANGDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | GSM+L900 | 112.2827 | -0.99818 | PT. Daya Mitra Telekomunikasi | SST | 2022-12-19 | SPS | BATTERY | Need SPS Recovery | 57.23 | 929.574 | OK |  | Not Achieve | P1 |  | 2026-10-14 |  |  | 2026-10-14 | Planned | Ya | OPEN
8 | KSN715 | KSN715_N3TPENDANANGEDMT | PLK | NOP PALANGKARAYA | BRONZE | 3 | SIMPUL MEDIUM | NA | NA | NA | NA | GSM+L900 | 112.2994 | -1.062 | PT. Daya Mitra Telekomunikasi | SST | 2022-12-16 | SPS | BATTERY | Need SPS Recovery | 75.4967 | 704.269 | OK |  | Not Achieve | P2 | Upgrade SPS Tsel by Relokasi SPS | 2026-10-09 |  |  | 2026-10-09 | Overdue | Ya | OPEN
9 | KSN716 | KSN716_N3TTUMBANGGAEIDMT | PLK | NOP PALANGKARAYA | BRONZE | 2 | SIMPUL KECIL | NA | NA | NA | NA | GSM+L900 | 112.2843 | -1.032 | PT. Daya Mitra Telekomunikasi | SST | 2022-12-19 | SPS | BATTERY | Need SPS Recovery | 75.0867 | 961.579 | OK |  | Not Achieve | P2 | Upgrade SPS Tsel by Relokasi SPS | 2026-10-13 |  |  | 2026-10-13 | Planned | Ya | OPEN
10 | KSN714 | KSN714_N3TTUMBANGMANANGEIDMT | PLK | NOP PALANGKARAYA | BRONZE | 5 | SIMPUL MEDIUM | NA | NA | NA | NA | DCS+GSM+L900+L1800 | 112.3619 | -1.175 | PT. Daya Mitra Telekomunikasi | SST | 2022-08-27 | SPS | BATTERY | Need SPS Recovery | 63.4833 | 1175.118 | OK |  | Not Achieve | P2 | Rectification SPS Tsel | 2026-10-11 |  |  | 2026-10-11 | Planned | Ya | OPEN
11 | NTH071 | NTH071_N3TTUMBANGKATAEIDMT | PLK | NOP PALANGKARAYA | BRONZE | 4 | SIMPUL MEDIUM | NA | NA | NA | NA | GSM+L900 | 112.3205 | -1.1123 | PT. Daya Mitra Telekomunikasi | SST | 2022-12-16 | SPS | BATTERY | Need SPS Recovery | 89.7367 | 877.848 | OK |  | Not Achieve | P3 | Rectification SPS Tsel | 2026-10-10 |  |  | 2026-10-10 | Overdue | Ya | OPEN
12 | NTH141 | N_NTH141_N3TTUMBANGKABAYANDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | GSM+L900 | 112.434 | -1.1307 | PT. Daya Mitra Telekomunikasi | SST | 2023-10-23 | SPS | BATTERY | Need SPS Recovery | 90.0767 | 851.952 | OK |  | Not Achieve | P3 | Rectification SPS Tsel | 2026-10-15 |  |  | 2026-10-15 | Planned | Ya | OPEN
13 | PRC191 | N_PRC191_N3TTELOKJOLODMT | PLK | NOP PALANGKARAYA | SILVER | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800 | 114.09 | -0.42968 | PT. Daya Mitra Telekomunikasi | SST | 2023-05-15 | SPS | BATTERY | Need SPS Recovery | 68.2667 | 1473.366 | >80% |  | Not Achieve | P1 | Upgrade SPS Tsel by Relokasi SPS | 2026-10-14 |  |  | 2026-10-14 | Planned | Ya | OPEN
14 | NTH086 | NTH086_N3TSEIBAKAUDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800 | 113.6193 | -3.403 | PT. Daya Mitra Telekomunikasi | SST | 2023-01-02 | SPS | BATTERY | Need SPS Recovery | 84.3433 | 1384.556 | >80% |  | Not Achieve | P2 | Rectification SPS Tsel | 2026-10-19 | 2026-10-10 | dibantu warga lokal pembersihan panel | 2026-10-19 | Done | Ya | DONE
15 | NTH073 | NTH073_N3TTUMBANGTUNDUDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | GSM+L900 | 112.5303 | -1.0592 | PT. Daya Mitra Telekomunikasi | SST | 2022-12-03 | SPS | BATTERY | Need SPS Recovery | 62.2833 | 1185.036 | OK |  | Not Achieve | P1 |  | 2026-10-16 |  |  | 2026-10-16 | Planned | Ya | OPEN
16 | NTH159 | N_NTH159_N3TBARUNANGDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | GSM+L900 | 114.3679 | -1.0912 | PT. Daya Mitra Telekomunikasi | SST | 0 | SPS | BATTERY | Need SPS Recovery | 92.4 | 875.115 | OK |  | Not Achieve | P3 | Rectification SPS Tsel | 2026-10-17 |  |  | 2026-10-17 | Planned | Ya | OPEN
17 | NTH160 | N_NTH160_N3TBINAJAYADMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | GSM+L900 | 114.4505 | -1.1288 | PT. Daya Mitra Telekomunikasi | SST | 0 | SPS | BATTERY | Need SPS Recovery | 93.42 | 854.49 | OK |  | Achieve | P3 | Rectification SPS Tsel | 2026-10-22 |  |  | 2026-10-22 | Planned | Ya | OPEN
18 | NTH074 | NTH074_N3TTUMBANGTAEIDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | GSM+L900 | 112.7173 | -1.1029 | PT. Daya Mitra Telekomunikasi | SST | 2022-11-29 | SPS | BATTERY | Need SPS Recovery | 59.2967 | 1369.135 | >80% |  | Not Achieve | P1 | Upgrade SPS Tsel by Relokasi SPS | 2026-09-15 | 2026-09-15 |  | 2026-09-15 | Done | Ya | DONE
19 | NTH269 | C_NTH269_N3T_MASUPARIADMT | PLK | NOP PALANGKARAYA | BRONZE | 1 | END SITE |  |  |  |  | L900 | 114.0473 | -0.55121 | PT. Daya Mitra Telekomunikasi | SST | 2026-05-18 | SPS | BATTERY | Need SPS Recovery | 84.92 |  | OK |  | Achieve | P3 |  | 2026-10-23 |  |  | 2026-10-23 | Planned | Tidak | -
20 | KSN721 | KSN721_N3TSELATBANINGDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 113.3475 | -3.2512 | PT. Daya Mitra Telekomunikasi | SST | 2022-05-30 | SPS | BATTERY | Need Upgrade SPS | 40.9367 | 1945.327 | >80% |  | Not Achieve | P1 | Upgrade SPS Tsel by Relokasi SPS | 2026-10-14 | 2026-10-10 |  | 2026-10-14 | Done | Ya | DONE
21 | KSN164 | KSN164_N3TBATUBANGODMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 112.5551 | -1.1792 | PT. Daya Mitra Telekomunikasi | SST | 2023-03-29 | SPS | BATTERY | Need Upgrade SPS | 56.1267 | 1921.316 | >80% |  | Not Achieve | P1 | Rectification SPS Tsel | 2026-09-16 | 2026-09-16 |  | 2026-09-16 | Done | Ya | DONE
22 | KKP293 | N_KKP293_N3TTUMBANGMUROIDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 114.4008 | -2.0238 | PT. Daya Mitra Telekomunikasi | SST | 2023-04-25 | SPS | BATTERY | Need Upgrade SPS | 82.31 | 1724.464 | >80% |  | Not Achieve | P2 | Upgrade SPS Tsel by Relokasi SPS | 2026-10-10 |  |  | 2026-10-10 | Overdue | Ya | OPEN
23 | KSN165 | KSN165_N3TKARUINGDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 113.394 | -2.3733 | PT. Daya Mitra Telekomunikasi | SST | 2022-05-30 | SPS | BATTERY | Need Upgrade SPS | 73.4833 | 1676.385 | >80% |  | Not Achieve | P2 | Rectification SPS Tsel | 2026-10-04 | 2026-10-04 |  | 2026-10-04 | Done | Ya | DONE
24 | NTH002 | NTH002_N3TPANTAILAGADMT | PLK | NOP PALANGKARAYA | SILVER | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 114.2547 | -0.589 | PT. Daya Mitra Telekomunikasi | SST | 2023-04-26 | SPS | BATTERY | Need Upgrade SPS | 45.26 | 1558.174 | >80% |  | Not Achieve | P1 | Rectification SPS Tsel | 2026-09-29 | 2026-09-29 |  | 2026-09-29 | Done | Ya | DONE
25 | NTH083 | N_NTH083_N3TTUMBANGMANGKETAIDMT | PLK | NOP PALANGKARAYA | BRONZE | 2 | SIMPUL KECIL | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 112.3889 | -1.1666 | PT. Daya Mitra Telekomunikasi | SST | 2023-05-27 | SPS | BATTERY | Need Upgrade SPS | 60.0933 | 1626.159 | >80% |  | Not Achieve | P2 | Rectification SPS Tsel | 2026-10-17 |  |  | 2026-10-17 | Planned | Ya | OPEN
26 | KKP311 | KKP311_N3THURUNGKAMPINDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 114.1511 | -1.1104 | PT. Daya Mitra Telekomunikasi | SST | 2023-01-27 | SPS | BATTERY | Need Upgrade SPS | 61.5833 | 1784.938 | >80% |  | Not Achieve | P1 | Rectification SPS Tsel | 2026-10-03 |  |  | 2026-10-03 | Overdue | Ya | OPEN
27 | NTH070 | NTH070_N3TTUMBANGNUSADMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 114.2451 | -1.0911 | PT. Daya Mitra Telekomunikasi | SST | 2023-02-05 | SPS | BATTERY | Need Upgrade SPS | 55.0333 | 1917.677 | >80% |  | Not Achieve | P1 | Upgrade SPS Tsel by Relokasi SPS | 2026-10-13 |  |  | 2026-10-13 | Planned | Ya | OPEN
28 | NTH075 | N_NTH075_N3TTUMBANGTIHISDMT | PLK | NOP PALANGKARAYA | SILVER | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 113.9961 | -0.73593 | PT. Daya Mitra Telekomunikasi | SST | 2022-12-31 | SPS | BATTERY | Need Upgrade SPS | 96.4167 | 1847.675 | >80% |  | Achieve | P3 | Upgrade SPS Tsel by Relokasi SPS |  |  | SPS sudah diupgrade disana sudah ada 2 sps |  | Belum dijadwalkan | Ya | OPEN
29 | NTH121 | N_NTH121_N3TBETANGNALONGDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 115.2858 | -2.0484 | PT. Daya Mitra Telekomunikasi | SST | 2023-01-06 | SPS | BATTERY | Need Upgrade SPS | 67.6467 | 1767.148 | >80% |  | Not Achieve | P2 |  | 2026-10-16 |  |  | 2026-10-16 | Planned | Ya | OPEN
30 | NTH125 | N_NTH125_N3TTARUSANDMT | PLK | NOP PALANGKARAYA | SILVER | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 114.8568 | -1.3814 | PT. Daya Mitra Telekomunikasi | SST | 2023-02-01 | SPS | BATTERY | Need Upgrade SPS | 87.5133 | 1849.816 | >80% |  | Not Achieve | P2 | Rectification SPS Tsel | 2026-10-17 |  |  | 2026-10-17 | Planned | Ya | OPEN
31 | NTH154 | NTH154_N3TRANGANBURIHDMT | PLK | NOP PALANGKARAYA | BRONZE | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 112.652 | -1.1605 | PT. Daya Mitra Telekomunikasi | SST | 0 | SPS | BATTERY | Need Upgrade SPS | 66.3 | 1837.558 | >80% |  | Not Achieve | P1 | Rectification SPS Tsel | 2026-10-28 |  |  | 2026-10-28 | Planned | Ya | DONE
32 | NTH153 | N_NTH153_N3TSEIGITADMT | PLK | NOP PALANGKARAYA | GOLD | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 114.3464 | -1.6788 | PT. Daya Mitra Telekomunikasi | SST | 0 | SPS | BATTERY | Need Upgrade SPS | 94.96 | 1796.646 | >80% |  | Not Achieve | P3 | Rectification SPS Tsel | 2026-10-03 | 2026-10-03 |  | 2026-10-03 | Done | Ya | DONE
33 | KKP325 | N_KKP325_N3TTANJUNGRENDANDMT | PLK | NOP PALANGKARAYA | SILVER | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 113.961 | -0.73757 | PT. Daya Mitra Telekomunikasi | SST | 2023-05-16 | SPS | BATTERY | Need Upgrade SPS | 90.4267 | 1547.835 | >80% |  | Achieve | P3 |  | 2026-10-18 |  |  | 2026-10-18 | Planned | Ya | OPEN
34 | NTH157 | NTH157_N3TJAKATANPARIDMT | PLK | NOP PALANGKARAYA | SILVER | 0 | END SITE | NA | NA | NA | NA | DCS+GSM+L900+L1800+L2100 | 114.1612 | -0.81038 | PT. Daya Mitra Telekomunikasi | SST | 2024-07-25 | SPS | BATTERY | Need Upgrade SPS | 90.3367 | 1663.392 | >80% |  | Not Achieve | P3 | Rectification SPS Tsel | 2026-10-20 | 2026-10-07 |  | 2026-10-20 | Done | Ya | DONE
Formulas:
Plan Date (baseline) = IF([SITEID]="","",IF(ISNUMBER([Plan Date Site Visit]),[Plan Date Site Visit],IF(ISNUMBER([Actual Date Visit]),[Actual Date Visit],"")))
Plan Date (baseline) = IF([SITEID]="","",IF(ISNUMBER([Plan Date Site Visit]),[Plan Date Site Visit],IF(ISNUMBER([Actual Date Visit, row below]),[Actual Date Visit, row below],"")))
Note on AF4: Plan Date; jika kosong tapi sudah visit, dipakai Actual Date (agar kurva plan tidak tertinggal dari actual).
Note on AG4: Done = Actual Date terisi; Overdue = Plan Date < Tanggal update (Dashboard!C4) dan belum ada Actual; Planned = Plan Date >= hari ini.
Note on B8: SITEID dikoreksi KSN165 → KSN188 dan nama site KSN188_N3TTUMBANGLAMBI (dikonfirmasi user, 5 Okt 2026).

## Kurva S
KURVA S — PERHITUNGAN (OTOMATIS, JANGAN DIKETIK)
Semua angka di sheet ini formula dari Tracker Improvement & Jadwal Visit SPS, mengikuti filter di Dashboard.
Kriteria Site Class | * |  | Kriteria Main Power | * |  | Kriteria Action Plan Visit | *
A. Kurva S Availability Improvement (mingguan, ISO week 2026)
Week | Mulai (Senin) | Label | Plan / minggu | Plan Kumulatif | Actual / minggu | Actual Kumulatif | % Plan Kum. (vs total site) | % Actual Kum. (vs total site) | Gap (Actual − Plan) | Achievement (Actual/Plan)
32 | 2026-08-03 | W32 | 1 | 1 | 1 | 1 | 0.4484% | 0.4484% | 0 | 100% | Total site (filter) | 223
33 | 2026-08-10 | W33 | 0 | 1 | 0 | 1 | 0.4484% | 0.4484% | 0 | 100% | Minggu berjalan | 41
34 | 2026-08-17 | W34 | 1 | 2 | 1 | 2 | 0.8969% | 0.8969% | 0 | 100% | Site dengan plan | 93
35 | 2026-08-24 | W35 | 1 | 3 | 1 | 3 | 1.345% | 1.345% | 0 | 100%
36 | 2026-08-31 | W36 | 2 | 5 | 2 | 5 | 2.242% | 2.242% | 0 | 100%
37 | 2026-09-07 | W37 | 6 | 11 | 6 | 11 | 4.933% | 4.933% | 0 | 100%
38 | 2026-09-14 | W38 | 3 | 14 | 3 | 14 | 6.278% | 6.278% | 0 | 100%
39 | 2026-09-21 | W39 | 24 | 38 | 3 | 17 | 17.04% | 7.623% | -21 | 44.74%
40 | 2026-09-28 | W40 | 15 | 53 | 15 | 32 | 23.77% | 14.35% | -21 | 60.38%
41 | 2026-10-05 | W41 | 17 | 70 | 13 | 45 | 31.39% | 20.18% | -25 | 64.29%
42 | 2026-10-12 | W42 | 14 | 84 | 0 | 45 | 37.67% | 20.18% | -39 | 53.57%
43 | 2026-10-19 | W43 | 3 | 87 | 0 | 45 | 39.01% | 20.18% | -42 | 51.72%
44 | 2026-10-26 | W44 | 2 | 89 | 0 | 45 | 39.91% | 20.18% | -44 | 50.56%
45 | 2026-11-02 | W45 | 4 | 93 | 0 | 45 | 41.7% | 20.18% | -48 | 48.39%
46 | 2026-11-09 | W46 | 0 | 93 | 0 | 45 | 41.7% | 20.18% | -48 | 48.39%
47 | 2026-11-16 | W47 | 0 | 93 | 0 | 45 | 41.7% | 20.18% | -48 | 48.39%
48 | 2026-11-23 | W48 | 0 | 93 | 0 | 45 | 41.7% | 20.18% | -48 | 48.39%
B. Kurva S Visit Site SPS (harian)
Tanggal | Label | Plan / hari | Plan Kumulatif | Actual / hari | Actual Kumulatif | % Plan Kum. | % Actual Kum.
2026-09-01 | 01/09 | 0 | 0 | 0 | 0 | 0% | 0% |  |  |  | Total site visit (filter) | 34
2026-09-02 | 02/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-03 | 03/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-04 | 04/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-05 | 05/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-06 | 06/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-07 | 07/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-08 | 08/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-09 | 09/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-10 | 10/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-11 | 11/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-12 | 12/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-13 | 13/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-14 | 14/09 | 0 | 0 | 0 | 0 | 0% | 0%
2026-09-15 | 15/09 | 1 | 1 | 1 | 1 | 2.941% | 2.941%
2026-09-16 | 16/09 | 1 | 2 | 1 | 2 | 5.882% | 5.882%
2026-09-17 | 17/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-18 | 18/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-19 | 19/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-20 | 20/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-21 | 21/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-22 | 22/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-23 | 23/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-24 | 24/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-25 | 25/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-26 | 26/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-27 | 27/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-28 | 28/09 | 0 | 2 | 0 | 2 | 5.882% | 5.882%
2026-09-29 | 29/09 | 1 | 3 | 1 | 3 | 8.824% | 8.824%
2026-09-30 | 30/09 | 0 | 3 | 0 | 3 | 8.824% | 8.824%
2026-10-01 | 01/10 | 0 | 3 | 0 | 3 | 8.824% | 8.824%
2026-10-02 | 02/10 | 0 | 3 | 0 | 3 | 8.824% | 8.824%
2026-10-03 | 03/10 | 4 | 7 | 2 | 5 | 20.59% | 14.71%
2026-10-04 | 04/10 | 1 | 8 | 1 | 6 | 23.53% | 17.65%
2026-10-05 | 05/10 | 0 | 8 | 0 | 6 | 23.53% | 17.65%
2026-10-06 | 06/10 | 0 | 8 | 0 | 6 | 23.53% | 17.65%
2026-10-07 | 07/10 | 1 | 9 | 1 | 7 | 26.47% | 20.59%
2026-10-08 | 08/10 | 1 | 10 | 0 | 7 | 29.41% | 20.59%
2026-10-09 | 09/10 | 1 | 11 | 0 | 7 | 32.35% | 20.59%
2026-10-10 | 10/10 | 3 | 14 | 3 | 10 | 41.18% | 29.41%
2026-10-11 | 11/10 | 1 | 15 | 1 | 11 | 44.12% | 32.35%
2026-10-12 | 12/10 | 1 | 16 | 0 | 11 | 47.06% | 32.35%
2026-10-13 | 13/10 | 2 | 18 | 0 | 11 | 52.94% | 32.35%
2026-10-14 | 14/10 | 3 | 21 | 0 | 11 | 61.76% | 32.35%
2026-10-15 | 15/10 | 1 | 22 | 0 | 11 | 64.71% | 32.35%
2026-10-16 | 16/10 | 2 | 24 | 0 | 11 | 70.59% | 32.35%
2026-10-17 | 17/10 | 3 | 27 | 0 | 11 | 79.41% | 32.35%
2026-10-18 | 18/10 | 1 | 28 | 0 | 11 | 82.35% | 32.35%
2026-10-19 | 19/10 | 1 | 29 | 0 | 11 | 85.29% | 32.35%
2026-10-20 | 20/10 | 1 | 30 | 0 | 11 | 88.24% | 32.35%
2026-10-21 | 21/10 | 0 | 30 | 0 | 11 | 88.24% | 32.35%
2026-10-22 | 22/10 | 1 | 31 | 0 | 11 | 91.18% | 32.35%
2026-10-23 | 23/10 | 1 | 32 | 0 | 11 | 94.12% | 32.35%
2026-10-24 | 24/10 | 0 | 32 | 0 | 11 | 94.12% | 32.35%
2026-10-25 | 25/10 | 0 | 32 | 0 | 11 | 94.12% | 32.35%
2026-10-26 | 26/10 | 0 | 32 | 0 | 11 | 94.12% | 32.35%
2026-10-27 | 27/10 | 0 | 32 | 0 | 11 | 94.12% | 32.35%
2026-10-28 | 28/10 | 1 | 33 | 0 | 11 | 97.06% | 32.35%
2026-10-29 | 29/10 | 0 | 33 | 0 | 11 | 97.06% | 32.35%
2026-10-30 | 30/10 | 0 | 33 | 0 | 11 | 97.06% | 32.35%
2026-10-31 | 31/10 | 0 | 33 | 0 | 11 | 97.06% | 32.35%
Formulas:
Mulai (Senin) = DATE(2025,12,29)+([Week]-1)*7
Week = [Week, row above]+1

## Ref ASR W39
REFERENSI — ACTION PLAN ASR W39 & SOW H2 ON GRID (NOP PALANGKARAYA)
Sumber: sheet "Sheet ASR", difilter NOP Palangkaraya. Kolom F:G dipakai Tracker kolom AC (Xcheck H2 SOW).
Site ID | Action Plan | NOP | Week | Site ID Action | SOW H2 ON GRID
KKP225 | Perbaikan Power -Check Cable Power | NOP PALANGKARAYA | W39 | BNT005 | Refinement FO Corporate
KKP217 | Automasi Genset | NOP PALANGKARAYA | W39 | BNT020 | FO_Corporate
NTH120 | SPS Troubleshoot | NOP PALANGKARAYA | W39 | BNT020 | FO_Corporate
NTH153 | SPS Troubleshoot | NOP PALANGKARAYA | W39 | COH082 | Refinement FO Telkom
|  |  |  | MTW037 | Swap Rectifier & Upgrade Battery
|  |  |  | MTW033 | Swap System
|  |  |  | COH956 | Refinement FO Telkom
|  |  |  | MTW059 | Swap System
|  |  |  | KKN004 | Rektifikasi Genset
|  |  |  | KKN006 | Rektifikasi Genset
|  |  |  | KKN004 | Rektifikasi Genset
|  |  |  | KKN049 | Swap System
|  |  |  | KKN222 | Upgrade Module & Battery
|  |  |  | KKN223 | Refinement FO Telkom
|  |  |  | KKN223 | Upgrade Battery
|  |  |  | KKP018 | Upgrade Module & Battery
|  |  |  | KKP026 | Upgrade Module & Battery
|  |  |  | KKP027 | Upgrade Module & Swap Battery
|  |  |  | PPS037 | Upgrade Module & Swap Battery
|  |  |  | KKP044 | Swap Rectifier & Upgrade Battery
|  |  |  | KKP045 | Upgrade Module & Battery
|  |  |  | KKP050 | Upgrade Module & Battery
|  |  |  | KKP052 | Refinement FO Telkom
|  |  |  | KKP052 | Upgrade Module & Battery
|  |  |  | KKP055 | Upgrade Module & Battery
|  |  |  | KKP070 | Refinement FO Telkom
|  |  |  | KKP070 | Upgrade Module & Battery
|  |  |  | KKP072 | Upgrade Module & Battery
|  |  |  | KKP082 | Upgrade Module & Battery
|  |  |  | KKP045 | Swap Rectifier & Upgrade Battery
|  |  |  | KKP088 | Vandalisme
|  |  |  | KKP065 | Upgrade Module & Battery
|  |  |  | KKP072 | Upgrade Module & Battery
|  |  |  | KKP095 | Refinement FO Telkom
|  |  |  | KKP095 | Upgrade Module & Battery
|  |  |  | KKP098 | Upgrade Module & Battery
|  |  |  | KKP102 | Upgrade Module & Battery
|  |  |  | KKP119 | Upgrade Module & Battery
|  |  |  | KKP195 | Refinement FO Telkom
|  |  |  | KKP072 | Upgrade Battery
|  |  |  | KKP225 | Upgrade Module & Battery
|  |  |  | KKP072 | Upgrade Module & Swap Battery
|  |  |  | KKP315 | Upgrade Module & Battery
|  |  |  | KKP072 | Upgrade Module & Battery
|  |  |  | KKP326 | Upgrade Module & Battery
|  |  |  | KKP072 | Upgrade Module & Battery
|  |  |  | KSN153 | Rektifikasi Genset
|  |  |  | KSN024 | Refinement FO Telkom
|  |  |  | KSN024 | Upgrade Module & Battery
|  |  |  | KSN028 | Refinement FO Telkom
|  |  |  | KSN028 | Upgrade Module & Battery
|  |  |  | KSN036 | Swap Battery
|  |  |  | KSN037 | Refinement FO Telkom
|  |  |  | KSN036 | Swap Rectifier & Upgrade Battery
|  |  |  | KSN126 | Upgrade Module & Battery
|  |  |  | KSN356 | Refinement FO Telkom
|  |  |  | KSN709 | Swap System
|  |  |  | KSN765 | Upgrade Module & Swap Battery
|  |  |  | KSN770 | Refinement FO Telkom
|  |  |  | KSN770 | Upgrade Module & Battery
|  |  |  | MTW011 | Upgrade Module & Battery
|  |  |  | MTW017 | Upgrade Module & Swap Battery
|  |  |  | MTW025 | Refinement FO Telkom
|  |  |  | MTW025 | Upgrade Module & Battery
|  |  |  | MTW033 | Swap Rectifier & Upgrade Battery
|  |  |  | MTW034 | Upgrade Module & Swap Battery
|  |  |  | MTW005 | Upgrade Module & Battery
|  |  |  | MTW136 | Refinement FO Telkom
|  |  |  | MTW169 | Upgrade Module & Battery
|  |  |  | MTW033 | Upgrade Battery
|  |  |  | NTH079 | Upgrade Module & Battery
|  |  |  | NTH081 | Upgrade Module & Battery
|  |  |  | NTH082 | Upgrade Module & Battery
|  |  |  | NTH085 | PSB PLN
|  |  |  | NTH119 | Upgrade Module & Battery
|  |  |  | NTH129 | Upgrade Daya PLN & Battery
|  |  |  | NTH245 | Upgrade Module & Battery
|  |  |  | NTH246 | Refinement FO Telkom
|  |  |  | NTH246 | Refinement FO Telkom
|  |  |  | NTH250 | Upgrade Module & Battery
|  |  |  | NTH261 | Refinement FO Telkom
|  |  |  | PRC166 | Upgrade Module & Battery
|  |  |  | PLK005 | Upgrade Module & Battery
|  |  |  | PLK025 | Swap System
|  |  |  | PLK839 | Refinement FO Telkom
|  |  |  | KKN075 | Upgrade Module & Battery
|  |  |  | KSN036 | Upgrade Module & Battery
|  |  |  | KSN036 | Swap System
|  |  |  | PPS094 | Rektifikasi Rectifer
|  |  |  | KSN036 | Upgrade Module & Battery
|  |  |  | PPS131 | Rektifikasi Rectifer
|  |  |  | PPS264 | Upgrade Daya PLN
|  |  |  | PRC002 | Refinement FO Telkom
|  |  |  | PRC002 | Upgrade Module & Battery
|  |  |  | PRC004 | Upgrade Module & Battery
|  |  |  | PRC014 | Refinement FO Telkom
|  |  |  | PRC016 | Upgrade Module & Battery
|  |  |  | PRC024 | Swap Rectifier & Upgrade Battery
|  |  |  | PRC051 | Swap System
|  |  |  | PRC138 | Power Corporate
|  |  |  | PRC166 | Refinement FO Telkom
|  |  |  | PRC166 | Upgrade Module & Battery
|  |  |  | PRC182 | Refinement FO Telkom
|  |  |  | PRC225 | Upgrade Module & Battery
|  |  |  | PRC226 | Upgrade Module & Battery
|  |  |  | PPS111 | Power Corporate
|  |  |  | PRC224 | Power Corporate
|  |  |  | TML032 | Swap Genset Tsel
|  |  |  | TML025 | Refinement FO Telkom
|  |  |  | TML032 | Swap Genset Tsel
|  |  |  | TML055 | Swap System
|  |  |  | TML127 | Upgrade Battery

## Ref Site Master
REFERENSI — SITE MASTER NOP PALANGKARAYA (SYSINFO SEP 2026)
Sumber: sheet "ALL SITE (sysinfo sep)". Kolom F otomatis: Ya jika site ada di Tracker Improvement.
SITEID | SITE NAME | DEPARTEMEN | TERITORY OPERATION | SITE CLASS | Ada di Tracker?
AMT003 | AMT003_JENAMAS | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
AMT101 | AMT101_DSRANTAUCMI | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT001 | BNT001_STOBUNTOKDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT002 | BNT002_IMACRO_BUNTOK2 | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
BNT003 | BNT003_TELUKBETUNGDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT004 | BNT004_PATAS | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT005 | BNT005_KALANISDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
BNT006 | BNT006_TABAKKANILAN | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT007 | BNT007_PENDANG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT008 | BNT008_MABUANDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT009 | BNT009_SABILAHBUNTOK | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT010 | BNT010_KALAHIEN | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT012 | C_BNT012_GUNUNGRANTAUDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT013 | BNT013_BUNTOK5 | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT015 | BNT015_BUNTOKKOTA | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT017 | BNT017_MENGKATIPILIR | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT019 | BNT019_DANAUSADARDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
BNT020 | BNT020_ADAROKLANIS | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
BNT025 | BNT025_RANGGAILUNGPTI | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
BNT026 | BNT026_JAYAKARSADMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT027 | BNT027_JALANASAMBUNTOKPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT028 | C_BNT028_IAASTOPBTELUKTIMBAUSCO | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT031 | BNT031_COMBATPTGAL | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
BNT036 | BNT036_TELUKTELAGAPTI | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
BNT041 | BNT041_KELADANTBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT042 | BNT042_SEWARGABUNTOK | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
BNT044 | BNT044_PALUREJOTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT045 | BNT045_BUNTOKBARITOTBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT047 | BNT047_JELAPATKARTINIDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT048 | BNT048_AMDBUNTOKDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
BNT049 | BNT049_BUNTOKPASARDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
BNT070 | C_BNT070_PENDAASAMTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT085 | BNT085_MERDEKABUNTOKPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT086 | BNT086_PANGLIMABATURBUNTOKPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT087 | BNT087_MULYABUNTOKDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT088 | BNT088_MERDEKABUNTOK2PTI | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
BNT105 | BNT105_KELADANBUNTOKCMI | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT109 | BNT109_DSSABABILAHCMI | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT110 | BNT110_DSBARUCMI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT160 | N_BNT160_PASARPATASDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER | Ya
BNT195 | BNT195_BANGKUANG2DMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
BNT202 | BNT202_B2BGALBAKUTASCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
BNT523 | BNT523_MANGKATIP | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
BNT524 | N_BNT524_TALIODMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT525 | BNT525_TELUKTIMBAUTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
BNT526 | BNT526_RAMPAMEADMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
BNT527 | N_BNT527_SMAADVENTTAMPARAKLAYUNGGMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
BNT528 | BNT528_RANGGAILUNG2TBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
COH030 | C_COH030_MI_DSHAJAKTSEL | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
COH036 | C_COH036_MIBAMBULUNGTSEL | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
COH049 | C_COH049_MIPELABUHANFERYPENDAHARATSEL | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH068 | C_COH068_MI_PASIR_PANJANGTSEL | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH069 | C_COH069_MI_LAHEITSEL | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
COH070 | C_COH070_COMBATPAMAASMINBARABARONANG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
COH082 | C_COH082_MIHPHDWIMA | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
COH087 | C_COH087_MITANJUNGPERAWAN | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH091 | C_COH091_MI_PKS_PT_ISATSEL | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
COH097 | COH097_COMKM30DMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
COH114 | COH114_PTMJCR | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
COH670 | C_COH670_MIDESATUMBANGRANDANGTSEL | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
COH671 | COH671_MULTITAMBANGJAYAUTAMA | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
COH822 | COH822_MI_PTTRIUMPDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH862 | COH862_PT_AGROLESTARI_SENTOSATSEL | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH902 | C_COH902_PTHPUBDASCO | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM | Ya
COH903 | C_COH903_SISEIHANYO | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH904 | COH904_COMBATVIPYANGTZERIVER | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH913 | C_COH913_PTMKMBASARANGESTATESCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
COH937 | C_COH937_COMBATRAFIISLAMICCENTER | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
COH941 | C_COH941_COMBAT_TUMBANGRUNGANTSEL | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH943 | C_COH943_COMBATPASARPUJON | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH944 | COH944_COMBAT_MATANANDAUTSEL | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH945 | C_COH945_SIPTISA1 | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
COH953 | C_COH953_SIPTISA2 | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
COH955 | C_COH955_PTTAMTAMAPERKASATSEL | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
COH956 | C_COH956_PTAGU MILLBUTONGTSEL | NOP PALANGKARAYA | TO BARITO RAYA | SILVER | Ya
COH957 | COH957_MINARUBUNDARANPUJON | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
COH959 | C_COH959_SIMALLPALANGKATSEL | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
COH961 | C_COH961_COMBATMASJIDAGUNGDARURRAHMANTSEL | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
COH969 | C_COH969_TUMBANG_PAJANGEHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
COH976 | C_COH976_MV_BUKITTUNGGALDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
COH979 | C_COH979_DUTAMALLPALANGKARAYA | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN001 | KKN001_KUALAKURUN | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKN002 | KKN002_SEPANGSIMIN | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN003 | KKN003_RUNGAN | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN004 | KKN004_TUMBANGTALAKEN | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKN005 | KKN005_TUMBANGMIRI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN006 | KKN006_TEWAH | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKN007 | KKN007_PEMDAKURUN | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN008 | KKN008_SARERANGANTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN009 | KKN009_PAMATANGLIMAUTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN010 | KKN010_TANJUNGRIU | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN011 | KKN011_KAMPURI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN012 | KKN012_TMBGMIWANTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN013 | KKN013_TANJUNGKARITAKTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKN014 | C_KKN014_B2BKALIMANTANHAMPARANSAWITSCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN016 | C_KKN016_BUNDARANSEPANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKN017 | KKN017_SANGKURUNDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN018 | N_KKN018_DAHIANTAMBUKPTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKN019 | KKN019_SEPANGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKN020 | N_KKN020_TANGKAHENDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN021 | KKN021_RABAMBANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN022 | C_KKN022_TELUKNYATUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN023 | KKN023_TBANGRHADMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN024 | KKN024_TANGKIDAHUYANPST | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN025 | KKN025_TUMBANGPASANGONGIHON | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKN027 | KKN027_JALANPOROSFAJARHARAPANPTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKN028 | C_KKN028_TUMBANGTARIAKDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN029 | KKN029_TUMBANGEMPAS2PTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKN031 | KKN031_JALEMURAYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN032 | KKN032_BANGUNSARITBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKN033 | KKN033_TARINGENTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKN034 | KKN034_MANUHINGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN035 | KKN035_DESAJALEMUPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN036 | C_KKN036_TELUK LAWAHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN037 | C_KKN037_BAKUTANGKUIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKN038 | C_KKN038_TUMBANGMARIKOIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKN039 | C_KKN039_IAAS MSAL_KEBUN3CSO | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKN040 | C_KKN040_IAAS_PPAMESSSKSSCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN043 | C_KKN043_TEHANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN044 | C_KKN044_LUWUKTUKAUTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKN045 | KKN045_PTKBAHANDANGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN046 | C_KKN046_IAAS MSAL_KEBUN4CSO | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKN048 | KKN048_STOKUALAKURUNDMT | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKN049 | KKN049_HURUNGBUNUTTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKN050 | KKN050_TAMPANGTUMBANGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKN054 | KKN054_PERINTISTEWAHPTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKN055 | KKN055_SIMPANGMIWAN | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKN056 | KKN056_LETJENDSUPRAPTOPTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKN061 | N_KKN061_BRINGEIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN062 | KKN062_DCKURUN | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN063 | KKN063_SANGKURUNDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN064 | KKN064_ANTANGTEWAHSTP | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN065 | KKN065_KASINTUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN070 | N_KKN070_DSSEPANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN071 | KKN071_BELAWANMULYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN072 | KKN072_TUMBANGMALAHOIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN073 | KKN073_LINTASTRANSDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN074 | KKN074_DSTUMBANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN075 | KKN075_KENDETDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN076 | KKN076_TUMBANGKAJUEIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN078 | KKN078_DSPILANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN079 | KKN079_SEPANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN081 | KKN081_PENDAPILANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN151 | KKN151_BODSTUMBANGTAMBIRAHTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN155 | KKN155_IMACRO_TUMBANGANJIRDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN158 | KKN158_KAMPURIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN178 | KKN178_KARYABAKTIRUNGANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKN191 | KKN191_TEWAHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN195 | KKN195_TUMBANGJUTUHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN222 | KKN222_FLORANUSAPERDANAPST | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN223 | KKN223_ARCHIPELAGOSTP | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKN224 | KKN224_TUMBANGHAKAUTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKN229 | N_KKN229_MSALPKSDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKN230 | KKN230_MULIASAWITAGROLESTARITBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKN231 | KKN231_AGROLESTARISENTOSATBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKN233 | KKN233_TEWANG_PAJANGANTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKP001 | KKP001_STOKUALAKAPUAS | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP002 | KKP002_DESALAMUNTIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP003 | KKP003_SELATHULU | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP004 | KKP004_BASARANG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP005 | KKP005_ANJIRHULU | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP006 | KKP006_SEITATAS | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP007 | KKP007_TIMPAH | NOP PALANGKARAYA | TO PALANGKARAYA | DIAMOND
KKP008 | KKP008_PUJON | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKP009 | KKP009_SEIHANYO | NOP PALANGKARAYA | TO PALANGKARAYA | DIAMOND
KKP010 | KKP010_ANJIRSERAPAT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP011 | KKP011_PULOTELO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP012 | KKP012_SELATDALAM | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP013 | KKP013_BATUNINDAN | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP014 | KKP014_MAMPULAU | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP016 | KKP016_TBSEITRAYATBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP017 | KKP017_MANUSUP | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP018 | KKP018_PENDAMUNTEITBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP019 | KKP019_MURUNGKERAMAT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP020 | KKP020_TAMBANBARUSELATAN | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP021 | KKP021_PLKUPANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP022 | KKP022_LUPAKDALAM | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP023 | KKP023_PALINGKAO | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP024 | KKP024_BASUNGKAI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP025 | KKP025_TALEKUNGPUNEI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP026 | KKP026_LAMUNTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP027 | KKP027_PUJONTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP028 | KKP028_HANDIWUNGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP029 | KKP029_TAJAHANHANTANGBERENGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP030 | KKP030_WARGAMULYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP031 | KKP031_GADABUNGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP032 | KKP032_KRYABAKTIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP033 | KKP033_PATIHRUMBIHPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP034 | KKP034_TBKATUNJUNGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KKP035 | KKP035_SAKATAMIANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP036 | KKP036_SETAJISELATDALAMPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP037 | KKP037_KAHAYANHILIRPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP038 | KKP038_SETAJISELATHILIRPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP039 | KKP039_SUKAMAJUTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP040 | KKP040_BATANJUNGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP041 | KKP041_TAMBANLUARDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP042 | KKP042_TAMBANCATURDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP043 | KKP043_SEIDUSUNDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP044 | KKP044_KAYUBULANPTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP045 | KKP045_TRANTANGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP046 | KKP046_MARAPITPTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP047 | KKP047_MAMPAIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP048 | KKP048_SEKATAMAKMURTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP049 | KKP049_SAYBARASTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP050 | KKP050_BUMIRAHAYUTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP051 | KKP051_PETAKBETUAHTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP052 | KKP052_IAAS_KRSSITEKSRTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP053 | KKP053_AYANIKM52PTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP054 | C_KKP054_TAMBANLUPAKTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP055 | C_KKP055_MVPASARTIMPAHPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP056 | KKP056_B2BKAPUASMAJUJAYASITETALAWANGSCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP057 | N_KKP057_TERUSANKARYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP058 | C_KKP058_B2BTRIOETAMAPERSADAKM56SCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP059 | C_KKP059_MANTANGAITENGAHTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP060 | KKP060_KAPUASBARIMBAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP061 | KKP061_DESAHAMPATUNGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP062 | KKP062_IMACRO_B2BTRIOETAMAPERSADA1SCO | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP063 | KKP063_DESASIDOREJOTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP064 | KKP064_SEIJANGKITDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP065 | KKP065_LUNGKOHLAYANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | DIAMOND | Ya
KKP066 | KKP066_PETAKPTIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP067 | KKP067_BKITBATUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP068 | KKP068_DANAURAWAHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP069 | KKP069_TUMBANGTUKUNTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KKP070 | N_KKP070_IMACRO_B2BTIMURSATRIAPERKASASCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP071 | KKP071_JALANBARITOPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP072 | KKP072_BAJUHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP074 | C_KKP074_SEIJANGKITCMI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP075 | N_KKP075_MASARAN_PENGKOLANTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP076 | C_KKP076_TBGDSANJIRKALAMPANTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP077 | KKP077_GANGLIMAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP078 | C_KKP078_GRAHAINTIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP079 | KKP079_JALANANGGREKPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP080 | KKP080_KAYUBULANTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP081 | C_KKP081_MARAPITLUARDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP082 | KKP082_HURUNGPUKUNGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP083 | KKP083_IAAS_TOPBMESSDURIANBUHUTSCO | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP084 | KKP084_IAAS_ASMIOFFICEASMINEWSCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP085 | C_KKP085_IAASTOPBSMKMAHARATISCO | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP086 | KKP086_IAAS_ASMISECTOR2SCO | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP087 | KKP087_DESAKALADAN | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP088 | C_KKP088_IAASASMISECTOR4SCO | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KKP089 | KKP089_IAAS_ASMISECTOR7SCO | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP090 | KKP090_IMACRO_ASMINBARABARONANGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | DIAMOND | Ya
KKP091 | KKP091_IAAS_ASMIHAULINGKM45SCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP092 | KKP092_IAAS_WANACATURJAYAUTAMATBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP093 | KKP093_DADAHUP | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP094 | KKP094_MANDOMAI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP095 | KKP095_MANTANGAI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP096 | KKP096_MUARADADAHUPPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP097 | KKP097_DWIWARNAKARYATBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KKP098 | C_KKP098_COMBATPAMACPP | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KKP100 | C_KKP100_WARGOMULYOTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP101 | KKP101_BELANTISIAM | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP102 | KKP102_BINJAYAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP103 | KKP103_CEMARALABATDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP104 | C_KKP104_PUJONSEBERANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP105 | KKP105_TRANSKALIMANTANKM14 | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP106 | KKP106_MV_BASARANGSPLIT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP107 | KKP107_KKAPUASPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP108 | C_KKP108_PTLIREFEAGROKAPUASSCO | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP113 | KKP113_SKBATURPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP114 | KKP114_MENTAREN1 | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP116 | KKP116_POLRESPULPISPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP117 | KKP117_KLUMPANPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP119 | KKP119_IMACRO_DAMANGSIMAN | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP120 | KKP120_SPLITPULANGPISAUPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP124 | KKP124_PULAUTELOPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP125 | KKP125_SUNGAIPASAHPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP126 | KKP126_JAWAKAPUASPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP127 | KKP127_GANGMENTARIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP128 | KKP128_DESAPALINGKAUSEJAHTERADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP130 | KKP130_KAPUASFERY | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP131 | KKP131_KAPUASGG3 | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP133 | KKP133_MASJIDMUKARRAM | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP134 | KKP134_ARUKDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP138 | KKP138_PANUNJUNGTARUNGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP139 | KKP139_JLPATIHRUMBIHPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP144 | KKP144_PULAUTELUTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP145 | KKP145_ANGGREKTENGAHTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP146 | KKP146_SANUSIPISAUTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP150 | KKP150_KERUINGKAPUASDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP151 | KKP151_MAHAKAMKAPUAS | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP156 | KKP156_DSTAJEPANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP157 | KKP157_DSBUNGAMAWARDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP158 | C_KKP158_DSBATUNINDANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP159 | KKP159_DSPANGKALANREKANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP190 | KKP190_B2BSUSANTIPERMAISCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP195 | KKP195_PTTOPSCO | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP197 | KKP197_DESAPANTAIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP199 | KKP199_KALIMANTANRIASEJAHTERASCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP208 | KKP208_ANJIRSERAPATDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP212 | KKP212_B2BKAPUASMAJUJAYASCO | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP217 | KKP217_N3TTABOREDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KKP218 | KKP218_N3TMASARANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP220 | KKP220_N3TBATUSAMBUNGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP222 | KKP222_N3TJAKATANMASAHADMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP223 | KKP223_CILIKRIWUTDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP225 | KKP225_TAPENDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP226 | KKP226_N3TLAHEIMANGKUTUPDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP227 | KKP227_N3TLAWANGKAJANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP228 | KKP228_N3TKABURANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP239 | KKP239_REPEATERRINJANISCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP241 | N_KKP241_N3TTUMBANGSIRATDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP293 | N_KKP293_N3TTUMBANGMUROIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KKP300 | KKP300_PERUMPULAUTELO | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP301 | KKP301_MURAIRAYA | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP304 | N_KKP304_N3TRAHUNGBUNGAIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KKP305 | KKP305_N3TSEIAHASDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP306 | KKP306_N3TTUMBANGMANGKUTUPDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KKP310 | KKP310_N3TBALAIBANJANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP311 | KKP311_N3THURUNGKAMPINDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KKP312 | KKP312_N3TSEIGAWINGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP314 | KKP314_N3TSEIRINGINDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP315 | KKP315_SEITERASTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP321 | C_KKP321_WARNASARIPST | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP323 | KKP323_B2BKMJMHESCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP324 | KKP324_B2BDWKGHE2SCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP325 | N_KKP325_N3TTANJUNGRENDANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP326 | KKP326_TIMPAHTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KKP339 | N_KKP339_B2BGLOBALINDOAGUNGLESTARIESTATELAMUNTITIMURSCO | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KKP340 | N_KKP340_B2BGLOBALINDOAGUNGLESTARIESTATEPLASMASCO | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KKP341 | N_KKP341_B2BGLOBALINDOAGUNGLESTARISITEESTATEUAISCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KKP342 | N_KKP342_B2BKAPUASMAJUJAYASITEPKSSCO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KKP343 | N_KKP343_SEITATASHILIRCMI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP344 | N_KKP344_ANJIRMAMBULAUPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KKP346 | KKP346_BASARANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN001 | KSN001_TUMBANGSENAMAN | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KSN002 | KSN002_TUMBANGHIRAN | NOP PALANGKARAYA | TO PALANGKARAYA | DIAMOND
KSN003 | KSN003_TUMBANGKAMAN | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KSN004 | KSN004_PMALAN | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN005 | KSN005_PETAKBAHANDANG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN006 | KSN006_BAUNBANGO | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN007 | KSN007_MENDAWAI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN008 | KSN008_PEGATAN | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN009 | KSN009_KATINGANHILIR | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN010 | KSN010_DESASAMBABAKUMPAIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN011 | KSN011_HAMPANGIN | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN012 | KSN012_BUKITBATU | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KSN013 | KSN013_POLRES | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN014 | KSN014_TALIANKERENG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN015 | KSN015_HAMPALIT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN016 | KSN016_BUPATIKASONGAN | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN017 | KSN017_KAMPUNGKERAMATTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN018 | KSN018_HANDIWUNGCMI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN019 | KSN019_KASONGANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN020 | KSN020_KERENGPANGI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KSN021 | KSN021_LUWUKNANTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN022 | KSN022_DESABANGUNJAYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN023 | KSN023_PENDAHARA | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN024 | KSN024_RANTAUASEMTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN025 | KSN025_KALANAMDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN027 | C_KSN027_KARYAUNGGANGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN028 | KSN028_DESATUMBANGKALEMEIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN030 | C_KSN030_BANDARATUMBANGSAMBACMI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN031 | KSN031_KM19HAMPALITTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KSN032 | KSN032_RANTAUBANGKIANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN035 | C_KSN035_TEWANGKAMPUNGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN036 | KSN036_MANGGODMT | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
KSN037 | KSN037_ADYAKSADHARMAKENCANATBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN039 | KSN039_RGTANGKOTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN040 | KSN040_IAAS_PERSADAAGROKENCANATBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN041 | KSN041_PETAKPUTIHPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN042 | KSN042_TEWANGRANGKANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN043 | KSN043_KAMPUNGTENGAHPST | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN046 | C_KSN046_DESA_TUMBANGKANEIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN048 | KSN048_MANGGOSELATANPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN050 | KSN050_KERENGBARATPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN052 | KSN052_NUKASONGANPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN053 | KSN053_DANAUMAREPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN055 | N_KSN055_HANTATIRINGESTATEPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN059 | KSN059_GRAPKASONGAN | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN067 | KSN067_PEMDAKATINGANTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KSN068 | KSN068_KASONGAN49DMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN069 | KSN069_KERENGKM13DMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN070 | KSN070_KERENGPANGI53DMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN071 | KSN071_TELANGKAHKUALAKURUN75DMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN072 | KSN072_SIMPANG3TUMBANGSAMBADMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN073 | KSN073_BAKUMPAISAMBADMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN110 | KSN110_DESAASEMKUMBANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN126 | KSN126_DESAJAYAMAKMUR | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN129 | KSN129_RANTAUBANGKIANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN135 | KSN135_DESASAMBAKATUNGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN136 | KSN136_KASONGANLAMATBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KSN137 | N_KSN137_TUMBANGLITINGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN138 | KSN138_DESATELANGKAHTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN140 | KSN140_TUMBANGLITINGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN147 | KSN147_N3TMAKMURUTAMADMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN150 | KSN150_N3TPENDATANGGARINGBARUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
KSN153 | N_KSN153_N3TTUMBANGBEMBANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN164 | KSN164_N3TBATUBANGODMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN165 | KSN165_N3TKARUINGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN188 | KSN188_N3TTUMBANGLAMBI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN193 | KSN193_N3TRANGANBAHEKANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN351 | KSN351_BODSTUMBANGLAHANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN356 | KSN356_KARYADEWIPUTRATBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN357 | KSN357_MANGGOTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN709 | KSN709_KM55PALANGKARAYA | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN710 | KSN710_TUMBANGSAMBA | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
KSN711 | KSN711_BATUBADINDINGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN713 | KSN713_RANTAUASEMDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN714 | KSN714_N3TTUMBANGMANANGEIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN715 | KSN715_N3TPENDANANGEDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN716 | KSN716_N3TTUMBANGGAEIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN720 | KSN720_N3TPARUPUKDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN721 | KSN721_N3TSELATBANINGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN722 | KSN722_N3TSEBANGAUJAYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
KSN762 | KSN762_MCMEBUPATIKASONGAN | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN763 | KSN763_PENDAHARAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN764 | KSN764_MV_DESATELOKCMI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
KSN765 | C_KSN765_TAWANGRANGASTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
KSN766 | KSN766_ARJUNAUTAMASAWITTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
KSN768 | N_KSN768_SIMPANGSAMBATBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN769 | N_KSN769_NAPUSAHURTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
KSN770 | KSN770_TUMBANGMARAKTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
MTW001 | MTW001_STOMUARATEWEHDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW002 | MTW002_MUARATEWE2PERWIRA | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW003 | MTW003_JALANNENAS | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
MTW004 | MTW004_STOHAJAK | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW005 | MTW005_KM64PURUKCAHUDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
MTW006 | MTW006_MALAWAKENPST | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
MTW007 | C_MTW007_B2BSATRIAALAMMANUNGGALSCO | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW009 | MTW009_PERTIWI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW010 | MTW010_WONOREJO | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW011 | C_MTW011_LUWEHULUDMT | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM | Ya
MTW012 | MTW012_PANDRANPERMAIPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW013 | MTW013_GUNUNGTIMANG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW014 | MTW014_GUNUNGPUREI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
MTW015 | MTW015_LAHEI | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM | Ya
MTW016 | MTW016_BENANGIN | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW017 | MTW017_TUMPUNGLAUNG | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM | Ya
MTW018 | C_MTW018_SI_B2B_AGU_KANDAUTSEL | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
MTW019 | C_MTW019_B2BPROSPEROSCO | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW020 | C_MTW020_IAASSMMSHAULINGKM9SCO | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
MTW021 | MTW021_IAAS_ASMIHAULINGKM25SCO | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW023 | MTW023_IAAS_SMMSHAULINGKM18SCOSCO | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW024 | MTW024_TBKAMAWENTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
MTW025 | C_MTW025_IAAS_AGU_PANDRANSCO | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
MTW026 | C_MTW026_IAAS_AGU_SIKANSCO | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
MTW029 | C_MTW029_PEPASTBG | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
MTW032 | MTW032_IAAS_SMMSMESSBARITHOSCO | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM | Ya
MTW033 | MTW033_BENAOTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
MTW034 | MTW034_LEMOTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
MTW035 | MTW035_RIMBASARITBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
MTW037 | MTW037_SIKUIKM30DMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW039 | MTW039_SABUHDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW041 | MTW041_BUANAADHITAMADMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW043 | MTW043_MERAKDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW047 | MTW047_BINTANGNINGGIPTI | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
MTW056 | MTW056_KANDUI | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
MTW059 | MTW059_BUTONG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW060 | MTW060_RUJIPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
MTW061 | MTW061_SIKUI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW062 | C_MTW062_TAMPARAKLAYUNG | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
MTW063 | MTW063_POLTEKMUARATEWEHPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
MTW066 | MTW066_MUARATEWEH10PTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW067 | MTW067_YETROSINSENGDMT | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
MTW069 | MTW069_LANJASPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW071 | MTW071_TRAHEANDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW072 | MTW072_BATURAYADMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
MTW073 | MTW073_NIHANDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW079 | MTW079_AYANITEWEH | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
MTW080 | MTW080_NUSAINDAHMTW | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW081 | MTW081_NUSAINDAHMTW2 | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
MTW082 | MTW082_IMACRO_PENDREHMTWTGM | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
MTW084 | MTW084_MELAYUMTEWEHDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
MTW085 | MTW085_PRAMUKATEWEHDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW086 | MTW086_BANDARATEWEHDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW087 | MTW087_PASARMUARADMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW088 | MTW088_PANGLIMABATURTEWEHDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW089 | MTW089_BUTONGDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW090 | MTW090_TRINSINGTBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW136 | MTW136_PAMASMMSCO | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
MTW138 | MTW138_SAWITSBMDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW169 | C_MTW169_MONTALLATTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
MTW172 | MTW172_B2BPTMULTIPERSADAGATRAMEGAHSCO | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
MTW176 | MTW176_TAWANJAYADMT | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM | Ya
MTW179 | MTW179_N3TSAMPIRANG2DMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
MTW180 | MTW180_N3TBENANGIN3DMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
MTW181 | MTW181_N3TLIJUDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
MTW206 | MTW206_PARINGLAHUNGTBG | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
MTW207 | N_MTW207_DESAPENDREHDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW242 | N_MTW242_MAJENGKANGTI | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
MTW248 | N_MTW248_IPUMELAYUPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
MTW249 | MTW249_TRINSINGTBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
MTW250 | N_MTW250_PERMATAHIJAUTBG | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
NTH002 | NTH002_N3TPANTAILAGADMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
NTH012 | N_NTH012_N3TBUNTUTLELENGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH037 | NTH037_N3TTANGIRANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
NTH044 | NTH044_N3TTUMBANGPAKUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH045 | NTH045_N3TMUROIRAYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
NTH047 | NTH047_N3TTUMBANGMALAWANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH053 | NTH053_N3TDIRUNGKORAMDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
NTH054 | NTH054_N3TBULAUNGANDUNGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
NTH058 | NTH058_N3TSUNGAILOBANGDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
NTH065 | N_NTH065_N3TSEIPINANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
NTH067 | NTH067_N3THURUNGTABENGANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
NTH070 | NTH070_N3TTUMBANGNUSADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH071 | NTH071_N3TTUMBANGKATAEIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH073 | NTH073_N3TTUMBANGTUNDUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH074 | NTH074_N3TTUMBANGTAEIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH075 | N_NTH075_N3TTUMBANGTIHISDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
NTH076 | NTH076_N3TTUMBANGMANDUREIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH079 | N_NTH079_N3TMUARAPARIDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
NTH080 | N_NTH080_N3TMANISDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
NTH081 | NTH081_N3TTUMBANGDIRINGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH082 | N_NTH082_N3TBARUNANG2DMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH083 | N_NTH083_N3TTUMBANGMANGKETAIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH085 | NTH085_N3TDANDANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
NTH086 | NTH086_N3TSEIBAKAUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH088 | N_NTH088_N3TSUBURINDAHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH112 | NTH112_N3TGERAGUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH114 | NTH114_N3TDEHESDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH115 | N_NTH115_N3TMARAGUTDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
NTH116 | N_NTH116_N3TLAGANDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
NTH117 | N_NTH117_N3TWURANDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
NTH118 | N_NTH118_N3TMUANIDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
NTH119 | NTH119_N3TMALUNGAIDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
NTH120 | NTH120_N3TMANGKAWUKDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH121 | N_NTH121_N3TBETANGNALONGDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
NTH123 | N_NTH123_N3TGANDRUNGDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
NTH124 | N_NTH124_N3TPANGKANDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
NTH125 | N_NTH125_N3TTARUSANDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER | Ya
NTH127 | N_NTH127_N3TJAHANJANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
NTH129 | N_NTH129_N3TPANAENDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
NTH138 | NTH138_N3TMUARAMARUWEIIIDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
NTH141 | N_NTH141_N3TTUMBANGKABAYANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH142 | NTH142_N3TSEBANGAUMULYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
NTH143 | NTH143_N3TTURADMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
NTH144 | NTH144_N3TTUMBANGRUNENDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
NTH147 | N_NTH147_N3THARARADMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
NTH148 | N_NTH148_N3TKALINAPUDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
NTH149 | N_NTH149_N3TJANAHJARIDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
NTH153 | N_NTH153_N3TSEIGITADMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
NTH154 | NTH154_N3TRANGANBURIHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH157 | NTH157_N3TJAKATANPARIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
NTH159 | N_NTH159_N3TBARUNANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH160 | N_NTH160_N3TBINAJAYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH245 | C_NTH245_N3TTANJUNGJAWADMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER | Ya
NTH246 | C_NTH246_BERENGMALAKADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
NTH247 | NTH247_N3TPAREMPEIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
NTH248 | NTH248_N3TBERENGBARUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
NTH249 | NTH249_N3TLUWUKLANGKUASDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
NTH250 | NTH250_N3TTUYUNDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
NTH252 | N_NTH252_N3T_BERONGDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
NTH253 | C_NTH253_N3T_SAMPIRANG IDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
NTH255 | N_NTH255_N3T_BATAPAHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
NTH261 | C_NTH261_N3T_MANGKAHUIDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
NTH262 | C_NTH262_N3T_BERIWITDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
NTH263 | C_NTH263_N3T_PARARAPAKDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
NTH267 | C_NTH267_N3T_TAMBABADMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
NTH269 | C_NTH269_N3T_MASUPARIADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK001 | PLK001_CENTRUMPLK | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK002 | PLK002_STOPALANGKARAYAKM5DMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK003 | PLK003_HMAHKOTA | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK004 | PLK004_IAAS_MITRAAGROPERSADAABADITBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK005 | C_PLK005_PETUKBARUNAIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PLK006 | PLK006_LANGKAI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK009 | C_PLK009_HABARINGHURUNGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK010 | PLK010_PALANGKARAYAKM12 | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
PLK011 | PLK011_JALANPIRANHACMI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK012 | PLK012_TUMBANGTAHAI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK013 | PLK013_DIPONEGOROPLKTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK014 | C_PLK014_TRANS_KM39_TANGKILINGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK015 | PLK015_OBOSMENTENGCMI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK017 | PLK017_LKBRBENGKEL | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK018 | PLK018_KM46PALANGKARAYA | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK019 | PLK019_SMP8PALANGKARAYA | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
PLK020 | PLK020_DIPONEGORO | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK021 | PLK021_YOSSUDARSO | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK022 | PLK022_GARUDA | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK023 | PLK023_KM7PALANGKARAYA | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK024 | PLK024_RAKUMPIT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK025 | PLK025_AddSect_TANGKILING | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
PLK027 | N_PLK027_KM17PALANGKARAYA | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK028 | PLK028_MILONOPLK | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK029 | PLK029_ASAMAD | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
PLK030 | PLK030_RAMIN | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK032 | PLK032_KBENGKIRAI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
PLK033 | PLK033_RRIPLK | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK034 | PLK034_BKEMINTING | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK035 | PLK035_ANTANG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK041 | PLK041_BANGARISDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK046 | PLK046_HOTELAQUARIUS | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK048 | PLK048_GOBOSDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK050 | PLK050_TELKOMAYANI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK051 | PLK051_PERUMMARINAPERMAIGTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK052 | PLK052_PEPABRILANGKAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK053 | PLK053_GGARUPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK054 | PLK054_RAMINPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK055 | PLK055_JALANKARANGGANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK056 | PLK056_PAULSULNGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK057 | PLK057_CILIKRIWUTDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK058 | PLK058_BETUTUPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK059 | PLK059_PANARUNG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK060 | PLK060_PAHANDUTPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK063 | PLK063_UNPARPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK065 | PLK065_BANGASTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK067 | PLK067_PERUMAHANLESTARIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK069 | PLK069_RAJAWALIKM3 | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK070 | PLK070_SANGGABUANA | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK071 | PLK071_KM6CILIKRIWUTDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK072 | PLK072_BKTTUNGGALPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK073 | PLK073_KM6PALANGKATBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK074 | PLK074_KINIBALUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK075 | PLK075_MUTIARATGLPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK077 | PLK077_CEMPAKADMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK079 | PLK079_SETAJITBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK080 | PLK080_GALAXYTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK082 | PLK082_RAJAWALITBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK083 | PLK083_SPLITBKEMINTINGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK086 | PLK086_SPLITRRIKAHAYANTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK090 | PLK090_DRMURJANIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK091 | PLK091_BATUSULIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK093 | PLK093_ANTANGINDUKDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK094 | PLK094_IMACRO_KERINCIPLKDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK098 | PLK098_BENGKIRAIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK099 | PLK099_TEMANGGUNGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK102 | PLK102_GOBOSPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK103 | PLK103_BERENGBENGKEL | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK105 | PLK105_PKYARGOPUPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK106 | PLK106_BUKITTUNGGALDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK111 | PLK111_GARUDATBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK115 | PLK115_MILONODMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK116 | PLK116_SIMPANGGALAXYPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK120 | PLK120_BANGAUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK121 | PLK121_RKYANIPLDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK124 | PLK124_BELIANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK141 | PLK141_BRIMOBTANGKILING | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK144 | C_PLK144_PAGERRAKUMPITDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK145 | PLK145_SAKANPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK146 | PLK146_MCPLKRUKOGALAXY | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK147 | PLK147_PASARBESARPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK148 | PLK148_SMA3PTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK149 | PLK149_HIURAYAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK151 | PLK151_OBOSPERMAIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK152 | PLK152_PKYLINTASKALIMANTANPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK155 | PLK155_MURAIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK156 | PLK156_BUNDERANGARUDAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK157 | PLK157_KALTENGPOSPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK158 | PLK158_KRAKATAUPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK159 | PLK159_PERUMAHANDPRDPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK162 | PLK162_SMAPANCASILAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK163 | PLK163_LELEPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK164 | PLK164_KEMINTINGKM2PTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK165 | PLK165_SIMPANGKEMINTINGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK166 | PLK166_PERUMNASPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK167 | PLK167_JALANLUMBA2PTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK168 | PLK168_PANGERANSAMUDRAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK171 | PLK171_SMK1PTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK172 | PLK172_MENTENGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK173 | PLK173_LUWANSAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK174 | PLK174_BEKOETINPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK175 | PLK175_KUTILANGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK176 | PLK176_AISNASUTIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK177 | PLK177_JALANBADAKPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK178 | PLK178_DRMURJANI2PTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK179 | PLK179_KALAWAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK180 | PLK180_MAHIRMAHARPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK191 | PLK191_DINASPU | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK192 | PLK192_SMA1PLK | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK193 | PLK193_IRIANPLK | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK195 | PLK195_TENDEAN | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK200 | PLK200_JEKANRAYAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK202 | PLK202_CEMARAPALANGKARAYAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK203 | PLK203_MAHIRMAHARPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK208 | PLK208_RTAMILONODMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK231 | PLK231_SIMPANGKARTINIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK232 | PLK232_SETHAJIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK234 | PLK234_URIAJAYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK235 | PLK235_RAUDAMILONODMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK236 | PLK236_JUNJUNGBUIHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK237 | PLK237_SAMUDINAMANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK238 | PLK238_RAKARTINI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK239 | PLK239_SANGGA_BUANADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK240 | PLK240_LAPASPALANGKADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK241 | PLK241_PASARKAHAYAN | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK242 | PLK242_IMACRO_KINIBALURAYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK243 | PLK243_RAJAWALIKM5DMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK245 | PLK245_CEMARARAYATBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK246 | PLK246_OBOSKEMINTINGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK247 | PLK247_TOKOCILIKRIWUT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK248 | PLK248_KERUINGPAHANDUTDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK250 | PLK250_BUKITINDAHTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK252 | PLK252_BELITUNGJAYATBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK254 | PLK254_ANGGREKBENGKIRAITBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK255 | PLK255_NYAIUNDANG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK256 | PLK256_MENTENGRAYATBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK259 | PLK259_BKTTTUNGGALTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK260 | PLK260_PINUSPERMAITBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK261 | PLK261_BROKOLITBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK262 | PLK262_KEMINTINGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK263 | PLK263_BUKITKOTIENDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK264 | PLK264_MCRDMSGONDO121 | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK265 | PLK265_GANGOBOS14TBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK266 | PLK266_TRANSGUBERNURDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK267 | PLK267_SETHADJI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK268 | PLK268_MENTENG18TBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK269 | PLK269_TANGKILING166TBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK271 | PLK271_TINGANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK272 | PLK272_BADAKDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK273 | PLK273_MENDAWAIKOTATBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK274 | PLK274_MANGKURAMBANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK275 | PLK275_PAHANDUTTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK277 | PLK277_DARMASUGONDODMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK278 | PLK278_GUBERNURPLKTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK600 | PLK600_HOTELAMARIS | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK708 | PLK708_TINGANG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK709 | PLK709_KAHAYAN | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK719 | PLK719_MENDAWAIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK722 | PLK722_KALIBATAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM
PLK726 | PLK726_BKTRAYAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK730 | PLK730_SKARUHEIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK732 | PLK732_DARMOSUGONDOPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK734 | PLK734_BUKITRAWI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK735 | PLK735_CILIKRIWUTK9PTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK748 | PLK748_MALLPLKSTP | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK810 | PLK810_SMP3PALANGKARAYATBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK813 | C_PLK813_METOSPLKSTP | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK814 | PLK814_TDCKAPUAS | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK816 | PLK816_TAMBUNBUNGAI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK818 | PLK818_TINGANGMANDIRIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK819 | PLK819_HIUPUTIHPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK820 | PLK820_PERWIRA | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK821 | PLK821_BABANPLK | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK825 | PLK825_JALANKARET | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK835 | PLK835_BERENGBENGKELDMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PLK839 | PLK839_N3TMUNGKUBARUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PLK841 | C_PLK841_PERUMCASSADOVA2TBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK842 | N_PLK842_CASSADOVAINDAHTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PLK849 | PLK849_BUKITRAWITBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PLK850 | N_PLK850_MARANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS001 | PPS001_GOHADMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS002 | PPS002_PULANGPISAU | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS003 | PPS003_GARANTUNGPANGKOHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS004 | PPS004_PADURANMULYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS005 | PPS005_KARYALUHURSEJATITBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
PPS006 | N_PPS006_KANAMITPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS007 | PPS007_KECAMATANMALIKU | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS008 | PPS008_BAWAN | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS009 | PPS009_BAHAUR | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS010 | N_PPS010_DESATARUNA | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS011 | PPS011_JABIREN | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS012 | PPS012_TJPINANG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS013 | PPS013_STOPULANGPISAUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS016 | C_PPS016_BAFMHAMBAWANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS017 | PPS017_MINTIN | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS019 | N_PPS019_DANDANGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS020 | C_PPS020_BUKITBAMBATBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS022 | PPS022_GARUNGTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS023 | PPS023_GANDANG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS026 | PPS026_SUKAJADIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS027 | PPS027_NUSAINDAHDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
PPS028 | PPS028_TAHAWADMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS029 | PPS029_LAWANGURUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
PPS030 | PPS030_PANGIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS031 | PPS031_TALMUARAPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS032 | C_PPS032_BADIRIHESTATE | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS037 | PPS037_SANAMANMANTIKEI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS045 | PPS045_PIPITPLK | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS054 | PPS054_HENDA | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS057 | PPS057_GOHONG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS060 | PPS060_PANGKUH | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS061 | PPS061_PETUKLITI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS062 | PPS062_PULANGJABIRENDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS065 | PPS065_SEBANGAUKUALA | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS077 | PPS077_PAHAWANPTI | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
PPS084 | PPS084_PTSCP2DMT | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
PPS094 | PPS094_TUMBANGDANAUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS095 | PPS095_PELABUHANTUMBANGEMPASPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS101 | PPS101_TUMBANGNUSA | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS102 | PPS102_TALIOHULUPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
PPS104 | PPS104_ABELGAWEPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS106 | PPS106_BLTSIAMPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS108 | PPS108_BARUNAIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS109 | PPS109_JABIREN46TBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS111 | PPS111_SAKTIMAITJAYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
PPS131 | PPS131_TAHAIJAYADMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER | Ya
PPS132 | PPS132_DSBAHUDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS134 | N_PPS134_PARAHANGANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS135 | PPS135_BERENGRAMBANGDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD
PPS136 | N_PPS136_DSBUNTOIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS137 | N_PPS137_DSPAMARUNANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS139 | PPS139_DESASIGIPTI | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS220 | PPS220_DSSUNGAIRUNGUNTBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS221 | PPS221_BODSBADIRIHTBG | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS222 | PPS222_DSGARANTUNGCMI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE | Ya
PPS223 | PPS223_DSKANAMITBARATCMI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS224 | PPS224_DSKANTANDALAMCMI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS226 | PPS226_DARUNBAWANDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS227 | PPS227_BUKITLITIDMT | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS235 | PPS235_DESAHANUABANAMADMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS247 | PPS247_BAHAURHILIRCMI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS250 | PPS250_KARYALUHURSEJATITBG | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS264 | PPS264_N3TTAMBAKDMT | NOP PALANGKARAYA | TO PALANGKARAYA | GOLD | Ya
PPS277 | PPS277_PTSURYAMASTBG | NOP PALANGKARAYA | TO PALANGKARAYA | PLATINUM | Ya
PPS280 | PPS280_MENTARENPST | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS281 | PPS281_SANGGANGCMI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS282 | N_PPS282_MINTINPTI | NOP PALANGKARAYA | TO PALANGKARAYA | SILVER
PPS283 | N_PPS283_GOHONGPTI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS284 | N_PPS284_KANTANMUARACMI | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PPS285 | PPS285_MULYASARITBG | NOP PALANGKARAYA | TO PALANGKARAYA | BRONZE
PRC001 | PRC001_STOPURUKCAHUDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
PRC002 | PRC002_MUARALAUNGITBG | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM | Ya
PRC003 | PRC003_MUARABUMBANTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
PRC004 | PRC004_TUMBANGLAHUTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
PRC005 | PRC005_KOMPLEKSDPR | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
PRC006 | PRC006_MARUNDA | NOP PALANGKARAYA | TO BARITO RAYA | SILVER | Ya
PRC007 | PRC007_TUMBANGLAHUNG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
PRC008 | PRC008_MUARALAUNG | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
PRC009 | PRC009_SARIPOI | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
PRC012 | PRC012_PURUKCAHU4QUNUT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
PRC013 | PRC013_PURUKCAHUSEBERANG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
PRC014 | C_PRC014_MUARAHTUHUPDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
PRC015 | PRC015_BERIWIT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
PRC016 | C_PRC016_B2BHARMONIPANCAUTAMASITESABSCO | NOP PALANGKARAYA | TO BARITO RAYA | SILVER | Ya
PRC017 | PRC017_DIRUNGLINGKIN | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM | Ya
PRC018 | PRC018_TUMBANGKUNYI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
PRC020 | N_PRC020_IMACRO_B2BHARMONIPANCAUTAMASITEMARUNDASCO | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
PRC023 | PRC023_BILITONTBG | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
PRC024 | PRC024_MUARAUTUTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
PRC025 | PRC025_TUMBANGMASAODMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
PRC026 | PRC026_BABUATDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
PRC029 | PRC029_BAHITOMTBG | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
PRC030 | PRC030_KOMPLEKRSUDTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
PRC038 | PRC038_TAHUJANONTUDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
PRC040 | PRC040_BONDANGPTI | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
PRC041 | PRC041_BUPATIPURUKCAHUPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
PRC043 | PRC043_KURUNPAJANGPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
PRC047 | PRC047_SENGAJI | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
PRC051 | PRC051_DESABAHITOM | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
PRC138 | PRC138_HARMONIPANCAUTAMATBG | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
PRC155 | PRC155_ADAROINDONESIALAMPUNUTSCO | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM
PRC166 | PRC166_DESAKONUTDMT | NOP PALANGKARAYA | TO BARITO RAYA | PLATINUM | Ya
PRC178 | PRC178_N3TLAKUTANDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
PRC182 | C_PRC182_PTAKT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
PRC187 | N_PRC187_N3TTEWAIHAUIDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
PRC189 | PRC189_N3TKALANGDOHONGDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
PRC190 | PRC190_N3TTUMBANGBALOIDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
PRC191 | N_PRC191_N3TTELOKJOLODMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
PRC200 | PRC200_DESABAHITOMDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
PRC224 | PRC224_PTSAPTAINDRASEJATISCO | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
PRC225 | N_PRC225_ISLAMICCENTERPRCTBG | NOP PALANGKARAYA | TO BARITO RAYA | DIAMOND | Ya
PRC226 | PRC226_MUARABAKANONTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
PRC227 | PRC227_JUKINGPANJANGDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML001 | TML001_TAMIANGLAYANGDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML002 | TML002_STOAMPAHDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML003 | TML003_JAAR | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML004 | TML004_BENTOT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
TML005 | TML005_BAMBULUNG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML007 | TML007_BARARAWADMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML008 | C_TML008_MURUTUWUDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML009 | TML009_TAMPA | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
TML010 | TML010_MRPLANTAUDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
TML011 | TML011_AMPKOTADMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
TML012 | TML012_DSNTIMURDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML013 | TML013_TELANGTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML014 | TML014_DORONGTBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML015 | C_TML015_NETAMPINDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
TML016 | TML016_TEWAHPPHDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML017 | TML017_DAYUTBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML018 | N_TML018_DDANGKAPTI | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML019 | TML019_MAMPAHKOTA | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML020 | C_TML020_TAMPA_PAKUCMI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML021 | TML021_UNSUMTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML025 | TML025_ADAROPASARPANAS | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML026 | TML026_AMPAHPATAS | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML027 | TML027_BANGKUANG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML028 | TML028_DAMPARAN | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML029 | TML029_HAYAPING | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML030 | TML030_JAWETAN | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML032 | TML032_SGRARAWA | NOP PALANGKARAYA | TO BARITO RAYA | SILVER | Ya
TML035 | TML035_KAMPUNGKARAMAHPTI | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML037 | TML037_PASIRPANASDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML038 | TML038_RNBATUAHDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML039 | TML039_KALAMUSTBG | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
TML040 | TML040_TAMIYANGDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML044 | TML044_AMPAHXLDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML055 | TML055_DESABAMBANDMT | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE | Ya
TML078 | TML078_DESAMATABUDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML082 | TML082_TBGDSPUTAITBG | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
TML112 | TML112_AYANIJAARDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML113 | TML113_PASARJAARDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML117 | TML117_PTBKITBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML119 | TML119_DSKEMPANGDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML127 | TML127_ISATTELANGBARUDMT | NOP PALANGKARAYA | TO BARITO RAYA | GOLD | Ya
TML160 | TML160_DESABENTOTTBG | NOP PALANGKARAYA | TO BARITO RAYA | BRONZE
TML161 | TML161_DESAPATUNGTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML167 | TML167_N3TDESADIDIDMT | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML180 | TML180_SAWITMANUNGGALTBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML236 | TML236_MATARAHTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD
TML237 | TML237_LENGGANGTBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML238 | TML238_HARINGENTBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML239 | TML239_SGMBUMIBORNEOESTATE2TBG | NOP PALANGKARAYA | TO BARITO RAYA | SILVER
TML240 | TML240_PERUMAHANTAMIYANGTBG | NOP PALANGKARAYA | TO BARITO RAYA | GOLD

## Lists
Action Status | Effort Cat | Impact Cat | Week Target | Site Class | Filter Site Class | Filter Main Power | Filter Action Plan Visit
OPEN | Low Effort | Low Impact | TBD | DIAMOND | (Semua) | (Semua) | (Semua)
ON GOING | Medium Effort | Medium Impact | Close | PLATINUM | DIAMOND | PLN | Need SPS Recovery
DONE | High Effort | High Impact | W36 | GOLD | PLATINUM | SPS | Need Upgrade SPS
|  |  | W37 | SILVER | GOLD | SPS TP
|  |  | W38 | BRONZE | SILVER | CORPORATE
|  |  | W39 |  | BRONZE | GENSET
|  |  | W40 |  |  | IN BUILDING
|  |  | W41 |  |  | PLN MULTIGUNA
W42
W43
W44
W45
W46
W47
W48
W49
W50
W51
W52
W53

## Catatan
CATATAN, CARA UPDATE & ASUMSI
Baca sebelum update data harian/mingguan.
STRUKTUR FILE
| Dashboard | Ringkasan NOP Palangkaraya: KPI, Kurva S Plan vs Actual (improvement & visit SPS), progres per kategori, cek kualitas data. Filter di sel kuning baris 4.
| Tracker Improvement | Data utama 223 site (dari sheet Site List). Input di kolom A–AD; kolom AE–AJ formula otomatis.
| Jadwal Visit SPS | Jadwal visit 34 site SPS NOP Palangkaraya (dari Sheet1; site NOP lain — BPP, PBUN, BJM, SMR — tidak dimasukkan). Input Plan Date (AC) & Actual Date (AD); kolom AF–AI otomatis.
| Kurva S | Tabel hitung untuk grafik (mingguan untuk improvement, harian 1 Sep–31 Okt untuk visit). Jangan diketik.
| Ref ASR W39 / Ref Site Master | Referensi dari file tracking (Sheet ASR dan ALL SITE sysinfo Sep), difilter NOP Palangkaraya (895 site master). Lists = isi dropdown.
CARA UPDATE
| 1. Update status | Ubah Action Status (OPEN / ON GOING / DONE) dan isi Date Actual di Tracker. Tanggal ketik sebagai tanggal (mis. 12-Oct-26), bukan teks "12 Okt".
| 2. Update plan | Week Target diisi format W41, W42, … (baseline target). Jika jadwal bergeser, isi Date Plan — baseline tidak berubah, pergeseran muncul di Flag "Reschedule".
| 3. Tambah site baru | Ketik/tempel di baris kosong tepat di bawah data terakhir (maks. baris 1004 Tracker / 304 Jadwal). Formula sudah tersedia sampai baris itu; Dashboard memberi peringatan bila ada data di luar jangkauan.
| 4. Visit SPS | Isi Plan Date Site Visit; setelah visit, isi Actual Date Visit. Status Visit (Done/Planned/Overdue) otomatis terhadap Tanggal update.
ASUMSI KURVA S
| Plan (Target) | Per site: Week Target (Wxx) → jika TBD/kosong pakai ISO week Date Plan → jika belum ada plan tapi sudah selesai, pakai minggu Date Actual. Kumulatif per ISO week 2026 (W1 mulai Senin 29 Des 2025).
| Actual | Site DONE bila Action Status = DONE, Week Target = Close, atau Date Actual terisi. Minggu actual = ISO week Date Actual; jika DONE tanpa tanggal, dipakai Plan Week.
| Visit SPS | Plan = Plan Date Site Visit (jika kosong tapi sudah visit, pakai Actual Date). Actual = Actual Date Visit. Kurva harian.
| Achievement | Actual kumulatif ÷ Plan kumulatif s.d. minggu/hari berjalan. Hijau ≥100%, oranye 80–99%, merah <80%.
PERUBAHAN DARI FILE ASLI
| Tanggal teks | Date Plan/Date Actual yang tertulis teks ("10 Okt 2026", "20 Sept", "5 Agust 2026") dikonversi ke tanggal asli; "-" dikosongkan. "20 Sept" tanpa tahun dianggap 2026.
| Irisan | Sebelumnya teks gabungan "YesYesYes"; kini jumlah program yang beririsan (0–4) dari kolom Repetitive/DPG/H2/Red Site.
| KSN165 → KSN188 | Sudah dikonfirmasi: baris KSN165 (Action Plan "Need SPS Recovery") di Jadwal Visit adalah KSN188. Nama site KSN188 diseragamkan menjadi KSN188_N3TTUMBANGLAMBI di Jadwal Visit, Tracker, dan Site Master (sebelumnya tertulis KSN165_N3TKARUINGDMT di sumber).
| Nilai error | Nilai error (N/A) di kolom Program H2 Area dan Load (NTH269) pada Jadwal dikosongkan.
| Cakupan PLK | File ini khusus NOP Palangkaraya: Jadwal Visit, Site Master, dan ASR hanya berisi site PLK; filter NOP diganti filter Action Plan visit.
| Sheet dihapus | pivot, Detail1, Sheet2 (copy Site List), Sheet1/Sheet2/Sheet3 jadwal (pivot & versi lama) — digantikan Dashboard yang otomatis.
LEGENDA WARNA
Header data (input)
Header kolom formula otomatis
Dropdown filter / perlu dicek
Minggu / hari berjalan